## 4 · PUNCH LIST
PS5 COMPLETION PLATFORM ¦ PUNCH LIST - 3094 item(s)
ID | TAG | CAT | DISC | DESCRIPTION | STATUS | CLOSE | SUB SYSTEM | ● | NOTES
PL-000073 | PS5-60-UR-8100A | C | M | Gen-Set nameplate and equipment tagging not complete. | Originated |  | PS5-60-01 - Power Generation Package A
PL-000074 | PS5-60-UR-8100B | C | M | Gen-Set nameplate and equipment tagging not complete. | Originated |  | PS5-60-04 - Power Generation Package B
PL-000075 | PS5-60-UR-8100C | C | M | Gen-Set nameplate and equipment tagging not complete. | Originated |  | PS5-60-07 - Power Generation Package C
PL-000076 | PS5-60-UR-8100D | C | M | Gen-Set nameplate and equipment tagging not complete. | Originated |  | PS5-60-10 - Power Generation Package D
PL-000077 | PS5-60-UR-8100E | C | M | Gen-Set nameplate and equipment tagging not complete. | Originated |  | PS5-60-13 - Power Generation Package E
PL-000078 | PS5-60-UR-8100F | C | M | Gen-Set nameplate and equipment tagging not complete. | Originated |  | PS5-60-16 - Power Generation Package F
PL-000079 | PS5-60-UR-8100G | C | M | Gen-Set nameplate and equipment tagging not complete. | Originated |  | PS5-60-19 - Power Generation Package G
PL-000170 | PS5-25-PA-3100A | C | M | CE mark not present on pump skid. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-000171 | PS5-25-PA-3100B | C | M | CE mark not present on pump skid. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-000172 | PS5-25-PA-3100C | C | M | CE mark not present on pump skid. | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-000173 | PS5-25-PA-3100A | A | M | Thermowells are to be replaced. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-000174 | PS5-25-PA-3100B | A | M | Thermowells are to be replaced. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-000175 | PS5-25-PA-3100C | A | M | Thermowells are to be replaced. | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-000176 | PS5-25-PA-3100A | B | M | PS5-25-LIT-3101A: Sunshade is damaged. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-000177 | PS5-25-PA-3100C | B | M | Sunshade has chips and appears to be damaged - Local to PS5-25-BI-1274C. | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-000178 | PS5-25-PA-3100C | 0 | M | PS5-25-BE-0001C: Stopping plugs installed into side of MTB frame do not have legible Ex markings | Closed | 2025-05-27 | PS5-25-04 - Crude Oil Export Pump C
PL-000327 | PS5-60-UR-8100D | A | M | 2: DAMAGED AIR FILTERS. | Closed | 2026-07-04 | PS5-60-10 - Power Generation Package D
PL-000329 | PS5-60-UR-8100D | A | M | 4:OIL LEAKAGE FROM GENERATOR BEARING LUBRICATION PUMP TUBING. | Closed | 2026-07-04 | PS5-60-10 - Power Generation Package D
PL-000330 | PS5-60-UR-8100D | B | M | 4.1:CABLE PROTECTION IS DAMAGED | Originated |  | PS5-60-10 - Power Generation Package D
PL-000331 | PS5-60-UR-8100D | A | M | 4.2:OIL LEAKAGE FROM DRAINING POINT | Closed | 2026-07-04 | PS5-60-10 - Power Generation Package D
PL-000332 | PS5-60-UR-8100D | A | M | 4.3: RUST IN SEVERAL AREAS OF GENSET AND PRESENCE OF PIN HOLES IN WELDING. | Closed | 2026-07-04 | PS5-60-10 - Power Generation Package D
PL-000333 | PS5-60-UR-8100D | C | M | 4.4:PAINT DAMAGED FROM LIFTING POINTS | Originated |  | PS5-60-10 - Power Generation Package D
PL-000334 | PS5-60-UR-8100C | A | M | 4:LEAKAGE FROM FUEL FILTER. | Closed | 2026-07-04 | PS5-60-07 - Power Generation Package C
PL-000335 | PS5-60-UR-8100C | C | M | 4.1:THE FUEL FILTER CONNECTING THREAD IS CORRODED | Originated |  | PS5-60-07 - Power Generation Package C
PL-000336 | PS5-60-UR-8100C | A | M | 4.2:THE BOTTOM HOLE ASSESORY IS DAMAGED | Originated |  | PS5-60-07 - Power Generation Package C
PL-000337 | PS5-60-UR-8100C | A | M | 4.3: TRANSMITTER ROD IS BEND AND OIL LEAKING | Closed | 2026-07-04 | PS5-60-07 - Power Generation Package C
PL-000338 | PS5-60-UR-8100C | A | M | 4.4:OIL LEAKAGE FROM DRAINING POINT | Closed | 2026-07-04 | PS5-60-07 - Power Generation Package C
PL-000339 | PS5-60-UR-8100C | C | M | 4.5:GENERATOR PAINT IRREGULARITY. | Originated |  | PS5-60-07 - Power Generation Package C
PL-000340 | PS5-60-UR-8100C | C | M | 4.6:BENDING OF THE HEAD CONNECTING PIPE IN ENGINE. | Originated |  | PS5-60-07 - Power Generation Package C
PL-000341 | PS5-60-UR-8100C | C | M | 4.7: RUST IN MULTIPLE LOCATIONS | Originated |  | PS5-60-07 - Power Generation Package C
PL-000342 | PS5-60-UR-8100C | C | M | 4.8:LIFTING POINT PAINT DAMAGE | Originated |  | PS5-60-07 - Power Generation Package C
PL-000343 | PS5-60-UR-8100B | A | M | 4:OIL LEAKAGE FROM SEVERAL PLACES OF GENERATOR.(TUBINGS,JOINTS) | Closed | 2026-07-04 | PS5-60-04 - Power Generation Package B
PL-000344 | PS5-60-UR-8100B | C | M | 4.1: RUST IN MULTIPLE AREAS | Originated |  | PS5-60-04 - Power Generation Package B
PL-000345 | PS5-60-UR-8100B | C | M | 4.2:PAINT DAMAGED AT LIFTING POINT | Originated |  | PS5-60-04 - Power Generation Package B
PL-000346 | PS5-60-UR-8100A | A | E | 4: A BUTTON ON GENERATOR CONTROL PANEL IS BROKEN | Originated |  | PS5-60-01 - Power Generation Package A
PL-000347 | PS5-60-UR-8100A | C | M | 4.1:RUST IN COUPLING AND OTHER PLACES. | Originated |  | PS5-60-01 - Power Generation Package A
PL-000348 | PS5-60-UR-8100A | A | M | 4.2:GENERATOR HAS MULTIPLE LEAKING POINTS.(JOINTS AND CONNECTIONS) | Closed | 2026-07-04 | PS5-60-01 - Power Generation Package A
PL-000349 | PS5-60-UR-8100A | C | M | 4.3:LIFTING POINTS PAINT DAMAGED | Originated |  | PS5-60-01 - Power Generation Package A
PL-000350 | PS5-60-UR-8100G | A | M | 4:LEAKAGE FROM MULTIPLE POINTS(JOINTS AND CONNECTIONS) | Closed | 2026-07-04 | PS5-60-19 - Power Generation Package G
PL-000351 | PS5-60-UR-8100G | C | M | 4.1:RUST IN MULTIPLE PLACES | Originated |  | PS5-60-19 - Power Generation Package G
PL-000352 | PS5-60-UR-8100G | C | M | 4.2:LIFTING POINTS PAINT ARE DAMAGED | Originated |  | PS5-60-19 - Power Generation Package G
PL-000353 | PS5-60-UR-8100A | A | E | 4.4: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | Originated |  | PS5-60-01 - Power Generation Package A
PL-000354 | PS5-60-UR-8100A | A | E | 4.5: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | Originated |  | PS5-60-01 - Power Generation Package A
PL-000355 | PS5-60-UR-8100B | A | E | 4.3: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | Originated |  | PS5-60-04 - Power Generation Package B
PL-000356 | PS5-60-UR-8100B | A | E | 4.4: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | Originated |  | PS5-60-04 - Power Generation Package B
PL-000357 | PS5-60-UR-8100C | A | E | 4.9: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | Originated |  | PS5-60-07 - Power Generation Package C
PL-000358 | PS5-60-UR-8100C | A | E | 4.10: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | Originated |  | PS5-60-07 - Power Generation Package C
PL-000359 | PS5-60-UR-8100D | A | E | 4.5: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | Originated |  | PS5-60-10 - Power Generation Package D
PL-000360 | PS5-60-UR-8100D | A | E | 4.6: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | Originated |  | PS5-60-10 - Power Generation Package D
PL-000361 | PS5-60-UR-8100G | A | E | 4.3: A jumper has been installed to short the CT at the alternator JB – Jumper to be removed once CTs will be connected and shorted at the CRO GCP via permanent cable. | Originated |  | PS5-60-19 - Power Generation Package G
PL-000362 | PS5-60-UR-8100G | A | E | 4.4: During preservation, VTs are disconnected in the cable terminal box to perform Insulation Resistance test. | Originated |  | PS5-60-19 - Power Generation Package G
PL-000363 | PS5-25-VP-1100 | B | P | 2: Check for any damage during transportation. | Closed | 2025-05-27 | PS5-25-01 - Export Pipeline Pig Receiver
PL-000364 | PS5-25-VP-1100 | C | M | Some areas inside the pig receiver are rust | Originated |  | PS5-25-01 - Export Pipeline Pig Receiver
PL-000365 | PS5-25-VP-1200 | C | M | Some place in the pig lancher is rust | Originated |  | PS5-25-07 - Export Pipeline Pig Launcher
PL-000423 | PS5-60-UR-8100E | B | M | 4:EXHAUST FLANGE IS NOT PAINTED. | Originated |  | PS5-60-13 - Power Generation Package E
PL-000424 | PS5-60-UR-8100E | A | M | 4.1:AIR INLET FILTER IS DAMAGED | Closed | 2026-07-04 | PS5-60-13 - Power Generation Package E
PL-000425 | PS5-60-UR-8100E | A | M | 4.2:THERE IS NO LUBE OIL INSIDE THE ALTERNATOR NON DRIVE END BEARING HOUSING. | Closed | 2026-07-04 | PS5-60-13 - Power Generation Package E
PL-000426 | PS5-60-UR-8100E | B | M | 4.3:THE FILTER HAS NO OIL INSIDE IT. | Originated |  | PS5-60-13 - Power Generation Package E
PL-000427 | PS5-60-UR-8100E | C | M | 4.4:THERE IS RUST INSIDE THE DAMPER AND SEVERAL PARTS OF THE GENERATOR . | Originated |  | PS5-60-13 - Power Generation Package E
PL-000428 | PS5-60-UR-8100E | A | M | 4.5:OIL LEAKAGE FROM MULTIPLE LOCATIONS | Closed | 2026-07-04 | PS5-60-13 - Power Generation Package E
PL-000429 | PS5-60-UR-8100E | C | M | 4.6:PAINT DAMAGED FROM BODY OF THE GENERATOR | Originated |  | PS5-60-13 - Power Generation Package E
PL-000430 | PS5-60-UR-8100E | C | M | 4.7:LIFTING POINT PAINT DAMAGED | Originated |  | PS5-60-13 - Power Generation Package E
PL-000431 | PS5-60-UR-8100F | B | E | 4:Jacket water heater control box button is damaged | Originated |  | PS5-60-16 - Power Generation Package F
PL-000432 | PS5-60-UR-8100F | B | M | 4.1:unavailability of oil in the filter | Originated |  | PS5-60-16 - Power Generation Package F
PL-000433 | PS5-60-UR-8100F | A | M | 4.2:low oil level in the NDE end of alternator side glass. | Closed | 2026-07-04 | PS5-60-16 - Power Generation Package F
PL-000434 | PS5-60-UR-8100F | C | M | 4.3:The head of the cam shaft cover plug bolt is damaged | Originated |  | PS5-60-16 - Power Generation Package F
PL-000435 | PS5-60-UR-8100F | C | M | 4.4:The generator has multiple rusts,Including damper | Originated |  | PS5-60-16 - Power Generation Package F
PL-000436 | PS5-60-UR-8100F | A | M | 4.5:The generator has multiple leakages | Closed | 2026-07-04 | PS5-60-16 - Power Generation Package F
PL-000437 | PS5-60-UR-8100F | C | M | 4.6:lifting points paint peeling; a little paint damage on the generator | Originated |  | PS5-60-16 - Power Generation Package F
PL-000467 | PS5-01-UK-6100 | C | M | 4:DOOR CANOPY IS DAMAGED | Originated |  | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100)
PL-000468 | PS5-01-UK-6100 | C | M | 4.1:THE KNOB OF THE EMERGENCY FIRE DOOR IS MISSING | Originated |  | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100)
PL-000469 | PS5-01-UK-6100 | C | M | 4.2: 4 DOOR KEYS ARE BEND | Originated |  | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100)
PL-000478 | PS5-25-MOV-0026 | B | I | Ensure that the mechanical stopper minimum flow through 25-MOV-0026 is higher than the export pump minimum flow. | Originated |  | PS5-25-01 - Export Pipeline Pig Receiver
PL-000479 | PS5-25-MOV-0027 | B | I | Ensure that the mechanical stopper minimum flow through 25-MOV-0027 is higher than the export pump minimum flow. | Originated |  | PS5-25-06 - Crude Oil Export Pumps Discharge
PL-000497 | PS5-05-UR-8100 | A | M | 4:THE TWO VIBRATION ISOLATORS, MEANT TO BE PLACED UNDER THE RADIATOR, HAVE BEEN MISTAKENLY INSTALLED BENEATH THE ENGINE. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000498 | PS5-05-UR-8100 | A | M | 4.1:LEVEL TRANSMITTER ON DIESEL TANK NOT INSTALLED. AND NOT FOUND ON LOCATION. REFERENCE PID TZ-MID-60-UTR2-130001_05. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000499 | PS5-05-UR-8100 | C | M | 4.2:CORROSION OBSERVED ON CASING OF THE TURBO CHARGER | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000500 | PS5-05-UR-8100 | A | E | 4.3:THE EMERGENCY LIGHT IS SEVERELY DAMAGED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000501 | PS5-05-UR-8100 | A | I | 4.4:THE FLAME DETECTOR IS NEITHER INSTALLED NOR SECURELY MOUNTED; INSTEAD, IT IS HANGING LOOSELY FROM THE CABLE TRAY IN DIESEL TANK ROOM. | Closed | 15-Aug-26 | PS5-05-01 - Emergency Diesel Generator Package
PL-000502 | PS5-05-UR-8100 | C | M | 4.5:AC FINS ARE PARTIALLY DAMAGED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000503 | PS5-05-UR-8100 | C | M | 4.6:EXHAUST PIPE SEALANT IS DAMAGED. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000504 | PS5-05-UR-8100 | C | M | 4.7:THE MONORAIL CRANE IS IMPROPERLY INSTALLED, WITH ITS WHEEL MISALIGNED AND OUT OF POSITION, CREATING A SIGNIFICANT RISK OF MALFUNCTION AND OPERATIONAL FAILURE | Completed |  | PS5-05-01 - Emergency Diesel Generator Package
PL-000505 | PS5-05-UR-8100 | C | M | 4.8:AC UNIT PLASTIC PIPE IS DEFORMED AND DAMAGED DUE TO THE CLAMP BEING OVERLY TIGHTENED. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000508 | PS5-05-UR-8100 | C | M | 4.9:CANOPY RUBBER PROTECTION IS MISSING. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000512 | PS5-05-UR-8100 | A | E | 4.10:2 EXTERNAL LIGHTS FOR MAIN DOORS (BRACKET BEND, LIGHT PROTECTION FALLEN OFF) | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000513 | PS5-05-UR-8100 | C | M | 4.11:ENGINE RADIATOR TO VENTILATION OUTLET CHAMBER NOT SEALED PROPERLY. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000514 | PS5-05-UR-8100 | C | M | 4.12:VENT OUTLET CHAMBER TO DAY TANK PARTITION WALL IS NOT PROPERLY SEALED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000515 | PS5-05-UR-8100 | C | M | 4.13:SUPPORT BEAM (FOR MONORAIL BEAM) FLANGE FACE IS HAVING GAPS | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000516 | PS5-05-UR-8100 | B | E | 4.14:EARTHING CABLE JUMPERS BETWEEN ELECTRICAL CABLE TRAYS ARE NOT EXISTING ON MANY LOCATIONS | Completed |  | PS5-05-01 - Emergency Diesel Generator Package
PL-000517 | PS5-05-UR-8100 | C | I | 4.15:INSTRUMENT CABLE RUNNING ON COOLING PIPE WITH TIE RODS | Originated |  | PS5-05-01 - Emergency Diesel Generator Package
PL-000518 | PS5-05-UR-8100 | A | I | 4.16:INSTRUMENT CABLE TERMINATION TO RADIATOR IS NOT PROPERLY FIXED. (NO CABLE INSULATION ) | Closed | 15-Aug-26 | PS5-05-01 - Emergency Diesel Generator Package
PL-000519 | PS5-05-UR-8100 | C | M | 4.17:THERE IS NO TAG NUMBER ON TROLLEY BEAM ,MANUAL TROLLEY & CHAIN BLOCKS | Completed |  | PS5-05-01 - Emergency Diesel Generator Package
PL-000520 | PS5-05-UR-8100 | A | M | 4.18:SPARE NOZZLE N3 ON DIESEL TANK HAS NO RATED BLIND, NO GASKET AND BOLT SETS. REFERENCE PID TZ-MID-60-UTR2-130001_05. | Closed | 2026-07-05 | PS5-05-01 - Emergency Diesel Generator Package
PL-000521 | PS5-05-UR-8100 | C | M | 4.19:NOZZLE 10 (FUEL FILLING WITH OVERFILL PREVENTION VALVE) FITTED WITH PTFE TAPE. REFERENCE PID TZ-MID-60-UTR2-130001_05. | Originated |  | PS5-05-01 - Emergency Diesel Generator Package
PL-000522 | PS5-05-UR-8100 | C | E | 4.20:LIGHTING JB DOES NOT HAVE TAG NUMBER JB DOES NOT HAVE MOISTURE ABSORBER (SUCH AS DESSICANT BAG- VPCI) | Originated |  | PS5-05-01 - Emergency Diesel Generator Package
PL-000523 | PS5-05-UR-8100 | A | E | 4.21:THERE IS NO “AIR SHUT OFF BUTTON” THERE IS NO PROTECTION CAP ON CABLE TERMINATION POINT. | Closed | 20-Aug-26 | PS5-05-01 - Emergency Diesel Generator Package
PL-000524 | PS5-05-UR-8100 | A | E | 4.22:KEYS FOR JB IS MISSING | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000525 | PS5-05-UR-8100 | C | M | 4.23:THE DOOR LOCK YIELDS ONLY WHEN TURNS AT AN ABSURD ANGLE. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000526 | PS5-05-UR-8100 | B | M | 4.24:THE AIR INLET HOOD FRAME IS SEVERELY DAMAGED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000527 | PS5-05-UR-8100 | C | M | 4.25:THE GASKET FOR THE INLET HOOD IS COMPLETELY TORN AND COMPROMISED. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000528 | PS5-05-UR-8100 | C | M | 4.26:AIR OUTLET HOOD FRAME IS SLIGHTLY BEND. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000529 | PS5-05-UR-8100 | A | M | 4.27:GLYCERINE LEAKAGE FROM THE HYDRAULIC CABIN PRESSURE GAUGE. THE GLYCERINE LEVEL INSIDE THE PG IS LOW. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000530 | PS5-05-UR-8100 | C | M | 4.28:OIL IS FOUND SPILLED ON THE BASE PLATE OF THE HYDRAULIC CABIN | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000531 | PS5-05-UR-8100 | C | M | 4.29:THE DAMPER COVER IN THE HYDRAULIC CABIN IS BEND. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000532 | PS5-05-UR-8100 | C | M | 4.30:HANDRAIL PAINT DAMAGED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000533 | PS5-05-UR-8100 | B | M | 4.3INSULATION ON MUFFLER FLANGE AREA ARE DAMAGED, NOT PROPERLY SEALED. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000534 | PS5-05-UR-8100 | B | M | 4.32:INSULATION DONE ON MUFFLER HAS MANY OPENING TO EXPOSED AIR. (SUCH AS LIFTING LUG, SUPPORT, CLADDING TO CLADDING AREAS) | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000535 | PS5-05-UR-8100 | C | M | 4.33:MUFFLER BOLTS AND NUTS ARE FULLY RUSTED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000536 | PS5-05-UR-8100 | C | M | 4.34:MUFFLER INSULATED SURFACES & FLANGES FOUND NOT PAINTED.IT SHOULD BE BLACK AS PER TZ-MID-60-UTR2-180023_02_AFC SECTION 4.6. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000537 | PS5-05-UR-8100 | C | M | 4.35:THE WELDING AND GRINDING ON THE MUFFLER EXHAUST PIPE ARE OF POOR QUALITY. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000540 | PS5-05-UR-8100 | C | M | 4.36:THE PIPE IN THE MUFFLER BOX , IS SHOWING SIGNS OF RUST AND IS UNPAINTED. | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000541 | PS5-05-UR-8100 | A | M | 4.37:WATER MIST CABINET N2 CYLINDERS DELIVERED WITH PRESSURE. (WE DONT KNOW WHAT TYPE OF GAS INSIDE) | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000542 | PS5-05-UR-8100 | A | M | 4.38:WATER MIST CABINET PTFE TAPE USED FOR THREADED JOINTS. (CYLINDER – VALVE CONNECTIONS) | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000546 | PS5-05-UR-8100 | A | M | 4.39:THE KEY SEEMS TO BE MALFUNCTIONING AND ISN'T OPENING THE DOOR | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000547 | PS5-05-UR-8100 | C | M | 4.40:WATER MIST CABINET PAINTED IN WHITE. IT SHOULD BE RED AS PER TZ-MID-60-WPR2-120001 (SECTION 6.2, PAGE 11/39) | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000548 | PS5-05-UR-8100 | C | M | 4.41:THERE IS A CRACK IN THE WELD OF THE MIST CABIN | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000549 | PS5-05-UR-8100 | C | M | 4.42:MIST CABIN AND MUFFLER PAINT DAMAGED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000550 | PS5-05-UR-8100 | C | M | 4.43:SPARE INSULATION , CLADDING (TO INSULATE AND CLAD MUFFLER RELATED JOINTS), ATTACHMENT BOLT SET, NOT RECEIVED, AND DETAILED PACKING LIST IS NOT AVAILABLE. | Originated |  | PS5-05-01 - Emergency Diesel Generator Package
PL-000564 | PS5-61-IDH-3100A | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | Closed | 2025-06-24 | PS5-25-02 - Crude Oil Export Pump A
PL-000565 | PS5-61-IDH-3100B | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | Closed | 2025-06-24 | PS5-25-03 - Crude Oil Export Pump B
PL-000566 | PS5-61-IDH-3100C | A | E | Revision to Sulzer/NIDEC wiring for VSD for the General Alarm and General Trips. | Closed | 2025-06-24 | PS5-25-04 - Crude Oil Export Pump C
PL-000612 | PS5-05-UR-8100 | A | M | Swapping of Radiator isolator/Engine isolator | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-000621 | PS5-60-UR-8100E | A | E | Potential transformer connection inside the alternator box | Originated |  | PS5-60-13 - Power Generation Package E
PL-000622 | PS5-60-UR-8100E | A | E | CTs at the alternator Juncon Box Jumpered (2CT1/2CT2) | Originated |  | PS5-60-13 - Power Generation Package E
PL-000623 | PS5-60-UR-8100F | A | E | Potential transformer connections inside the | Originated |  | PS5-60-16 - Power Generation Package F
PL-000624 | PS5-60-UR-8100F | A | E | CTs at the alternator Juncon Box are Jumpered (2CT1/2CT2) | Originated |  | PS5-60-16 - Power Generation Package F
PL-000702 | PS5-61-IU-3100A | C | M | 4:Found radiator bottom and top angle bar support bolt & nuts need to be tighted properly. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-000703 | PS5-61-IU-3100A | C | M | 4.1:Found all transformer radiator support paint need to be provided | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-000704 | PS5-61-IU-3100B | C | M | 4:Found radiator bottom area unpainted steel angle bar support need to be painted | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-000705 | PS5-61-IU-3100B | C | M | 4.1:Found all transformer radiator support paint need to be provided | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-000706 | PS5-61-IU-3100C | C | M | 4:Found radiator bottom and top angle bar support bolt & nuts need to be tighted properly. | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-000707 | PS5-61-IU-3100C | C | M | 4.1:Found all transformer radiator support paint need to be provided | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-000711 | PS5-71-PA-3100A | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | Originated |  | PS5-71-16 - Diesel Fuel Supply Pump A/B
PL-000712 | PS5-71-PA-3100B | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | Originated |  | PS5-71-16 - Diesel Fuel Supply Pump A/B
PL-000713 | PS5-71-PA-3200 | A | M | 4:CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000720 | PS5-60-UA-5100 | C | M | 4:THE WOODEN CRATE IS COMPLETELY SHATTERED. | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-000721 | PS5-60-UA-5100 | B | M | 4.1:THE PRESSURE GAUGE IS SLIGHTLY BENT DUE TO THE IMPACT FROM THE BROKEN WOODEN CRATE. | Closed | 2026-07-09 | PS5-60-27 - Compressed Air Starting Skid
PL-000722 | PS5-60-UA-5100 | C | M | 4.2:SOME OPENINGS ARE IMPROPERLY PLUGGED | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-000723 | PS5-60-UA-5100 | A | M | 4.3:THE HEAT EXCHANGER PIPE IS BROKEN FROM THE COMPRESSOR HEAD. | Closed | 2026-07-04 | PS5-60-27 - Compressed Air Starting Skid
PL-000724 | PS5-60-UA-5100 | B | M | 4.4:NO PROPER PACKING LIST PROVIDED FOR COMMISSIONING SPARES | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-000725 | PS5-60-UA-5100 | C | M | 4.5:TRACES OF COOLANT FOUND ON THE TOP OF THE COOLANT TANK | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-000726 | PS5-60-UA-5100 | C | M | 4.6:SOME PARTS ARE COMPLETELY RUSTED | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-000727 | PS5-60-UO-81100A | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | Completed |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-000728 | PS5-60-UO-81100B | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | Completed |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-000729 | PS5-60-UO-81100C | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | Completed |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-000730 | PS5-60-UO-81100D | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | Completed |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-000731 | PS5-60-UO-81100E | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | Completed |  | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E
PL-000732 | PS5-60-UO-81100F | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | Completed |  | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F
PL-000733 | PS5-60-UO-81100G | C | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED | Completed |  | PS5-60-55 - Lube Oil Separator Module PS5-60-UO-81100G
PL-000734 | PS5-60-UZ-8200A | C | M | 4:THE PAINT ON THE INJECTOR TIP COOLING MODULE FLANGE IS CRACKED | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-000735 | PS5-60-UZ-8200A | C | M | 4.1:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-000736 | PS5-60-UZ-8200B | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-000737 | PS5-60-UZ-8200C | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-000738 | PS5-60-UZ-8200D | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-000739 | PS5-60-UZ-8200E | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | Originated |  | PS5-60-39 - Injector Tip Cooling Module E
PL-000740 | PS5-60-UZ-8200F | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED | Originated |  | PS5-60-40 - Injector Tip Cooling Module F
PL-000741 | PS5-60-VS-9100A | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | Closed | 2026-07-09 | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-000742 | PS5-60-VS-9100B | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | Closed | 2026-07-09 | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-000743 | PS5-60-VS-9100B | B | M | 4.1:WATER INGRESS HAS BEEN DETECTED INSIDE THE MIST ELIMINATOR AND THE MOTOR | Originated |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-000744 | PS5-60-VS-9100C | B | M | 4:WATER INGRESS HAS BEEN DETECTED INSIDE THE MIST ELIMINATOR AND THE MOTORS. | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-000745 | PS5-60-VS-9100C | B | M | 4.1:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-000746 | PS5-60-VS-9100D | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | Originated |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-000747 | PS5-60-VS-9100E | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | Originated |  | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E
PL-000748 | PS5-60-VS-9100F | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | Originated |  | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F
PL-000749 | PS5-60-VS-9100G | B | M | 4:SIGNS OF RUST HAVE BEEN OBSERVED INSIDE ALL THE MOTORS OF THE MIST ELIMINATOR, INDICATING POSSIBLE EXPOSURE TO MOISTURE | Originated |  | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G
PL-000750 | PS5-71-UZ-6500 | A | E | 4:THE JB DOOR OF THE DO SEPARATOR IS NOT FIXED, AND THE BOLTS ARE MISSING. | Originated |  | PS5-71-18 - Diesel Separator Module
PL-000751 | PS5-71-UZ-6800A | C | M | 4:SOME OPENINGS ARE IMPROPERLY PLUGGED | Originated |  | PS5-71-06 - Crude Fuel Separation Module
PL-000752 | PS5-71-UZ-6800A | B | M | 4.1:THE PSV AND FIT WERE IMPROPERLY SECURED, AND WE DISCOVERED THE PSV CARELESSLY DISPLACED, LYING UPSIDE DOWN ON THE GROUND.(NEED TO BE INSTALLED) | Closed | 2026-07-04 | PS5-71-06 - Crude Fuel Separation Module
PL-000753 | PS5-71-UZ-6800A | A | M | 4.2:THE FCV IS NOT CONNECTED ON A SINGLE SIDE. | Closed | 2026-07-04 | PS5-71-06 - Crude Fuel Separation Module
PL-000754 | PS5-71-UZ-6800A | A | E | 4.3:Control panel key is missing. | Originated |  | PS5-71-06 - Crude Fuel Separation Module
PL-000755 | PS5-71-UZ-6800B | A | E | 4:CONTROL PANEL KEY IS MISSING | Originated |  | PS5-71-06 - Crude Fuel Separation Module
PL-000756 | PS5-71-UZ-6800B | B | M | 4.1:NO LUBE OIL AVAILABLE AT THE VIEWING GLASS. | Originated |  | PS5-71-06 - Crude Fuel Separation Module
PL-000757 | PS5-71-UZ-6800B | C | M | 4.2:A LOT OF OPENINGS ARE NOT PROPERLY PLUGGED | Originated |  | PS5-71-06 - Crude Fuel Separation Module
PL-000758 | PS5-71-UZ-6800B | A | M | 4.3:THE PSV, FLOW GAUGE, AND SPOOLS ARE NOT INSTALLED AND LYING ON THE GROUND. (NEED TO BE INSTALLED) | Closed | 2026-07-04 | PS5-71-06 - Crude Fuel Separation Module
PL-000759 | PS5-60-UZ-8200G | C | M | 4:THE INJECTOR TIP COOLING MODULE HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED. | Originated |  | PS5-60-41 - Injector Tip Cooling Module G
PL-000760 | PS5-28-VDC-1100 | A | M | 4:THE INSULATION RING FOR THE CLOSED DRAIN DRUM IS DAMAGED. | Closed | 2025-05-27 | PS5-28-03 - Closed Drain Drum and Pump 01
PL-000761 | PS5-28-VDC-1100 | C | M | 4.1:THE CLOSED DRAIN DRUM EXHIBITS PAINT DAMAGE. | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-000762 | PS5-28-VDC-1100 | B | M | 4.2:NO PACKING NOTE AVAILABLE FOR COMM. & STARTUP SPARES . FOUND- 4INCH 150 ASME GASKET(QUANTITY-1), REGULATOR KNOB, 1 BOLT, 10 STUD BOLT & 20 HEX NUT, 4INCH 150 ASME GASKET(QUANTITY -6) 2 MANUAL. | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-000763 | PS5-71-UZ-6200 | C | M | 4:THE CONTAINER IS DAMAGED | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000764 | PS5-71-UZ-6200 | C | M | 4.1:THE CONTAINER HAS SIGNIFICANT PAINT DAMAGE. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000765 | PS5-71-UZ-6200 | A | E | 4.2:THE TUBE LIGHT FELL FROM ITS ORIGINAL POSITION AND GOT DAMAGED | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000766 | PS5-71-UZ-6200 | C | M | 4.3:THE SPOOL FROM THE DISPENSER HAS PAINT DAMAGE. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000767 | PS5-71-UZ-6200 | A | M | 4.4:THE METALLIC FLEXIBLE CONNECTION IS BROKEN AND DAMAGED. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000768 | PS5-71-UZ-6200 | C | M | 4.5:THE DISPENSER COVERS ARE NOT PROPERLY MOUNTED AND HAVE FALLEN TO THE GROUND. | Completed |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000769 | PS5-71-UZ-6200 | B | M | 4.6:THE GASKET FOR THE SIDE VIEWING GLASS IS DAMAGED. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000770 | PS5-71-UZ-6200 | C | M | 4.7:THE NUT & BOLT FOR THE SIDE VIEWING GLASS IS MISSING. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000771 | PS5-71-UZ-6200 | C | M | 4.8:THE ROLLING WIRE IS COMPRESSED BENEATH THE STRUCTURE. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000772 | PS5-71-UZ-6200 | C | M | 4.9:THE FLOW INDICATOR TRANSMITTER IS NOT MOUNTED OR BOLTED SECURELY. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000773 | PS5-71-UZ-6200 | B | M | 4.10:OPENED THE ROOF HATCH, BUT THE KEY IS STILL NOT WORKING; LOCK & KEY NEEDS TO BE REPLACED | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000774 | PS5-71-UZ-6200 | C | M | 4.11:THE INLET SPOOL FOR THE VESSEL IS NOT MOUNTED PROPERLY. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000775 | PS5-71-UZ-6200 | B | E | 4.12:THE CABLE LAID IN THE WALKWAY NEEDS TO BE REMOVED AND PROPERLY ORGANIZED IN THE CABLE TRAY/CHANNEL. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000776 | PS5-71-UZ-6200 | A | E | 4.13:THE CABLE NEEDS TO BE PROTECTED FROM SHARP EDGES. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000777 | PS5-71-UZ-6200 | C | M | 4.14:THE CHANNEL SHOULD BE FIXED SECURELY ON BOTH ENDS WITH SCREWS, AND A WIRE TAG SHOULD BE PROVIDED | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000778 | PS5-71-UZ-6200 | C | E | 4.15:ALL THE PAPER TAG SHOULD BE REPLACED WITH A STAINLESS STEEL (SS) TAG | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000779 | PS5-71-UZ-6200 | C | E | 4.16:ALL INSTRUMENT HANGING TAG (SS TAG) SHOULD BE PROVIDED. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000780 | PS5-71-UZ-6200 | C | M | 4.17:THE DISPENSER IS NOT SECURELY FIXED AND IS SHAKING. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000781 | PS5-71-UZ-6200 | B | M | 4.18:OPENED THE TECHNICAL ROOM DOOR; THE DOOR LOCK WAS JAMMED AND NOW IS WORKING, BUT NOT SMOOTHLY. THE LOCK COVER IS DAMAGED AND NEED TO BE REPLACED, AND THE DOOR FRAME IS NOT FIXED PROPERLY, RESULTING IN HEAVY SHAKING. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000782 | PS5-71-UZ-6200 | A | E | 4.19:THE TUBE LIGHT HAS FALLEN FROM ITS ORIGINAL POSITION AND IS HANGING IN THE TECHNICAL ROOM. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000783 | PS5-71-UZ-6200 | C | M | 4.20:TWO NUT BOLTS ARE MISSING FROM THE M LADDER SUPPORT. | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-000812 | PS5-60-UR-8100A | C | M | 4:THERE IS A SLIGHT BEND ON THE BODY OF THE ADAPTOR(ADAPTOR Ø650 to Øout 508 L1280 - inlet engine ) | Originated |  | PS5-60-01 - Power Generation Package A
PL-000813 | PS5-60-UR-8100A | C | M | 4.1:TWO OF THE STRAIGHT LENGTHS ARE BENT IN THREE PLACES(ADJUSTABLE STRAIGHT LENGTH L2850- 3000mm Ø650) | Originated |  | PS5-60-01 - Power Generation Package A
PL-000814 | PS5-60-UR-8100A | C | M | 4.2:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA ,Gaps not properly filled/sealed, Partially used mastic to seal which have not working(STRAIGHT LENGTH L10000mm DIA 950/1150 EXHAUST LINE) | Originated |  | PS5-60-01 - Power Generation Package A
PL-000815 | PS5-60-UR-8100A | B | M | 4.3:A SMALL CUT WAS FOUND ON THE OUTER COVER OF THE STRAIGHT LENGTH L10000mm DIA 950/1150 EXHAUST LINE | Originated |  | PS5-60-01 - Power Generation Package A
PL-000816 | PS5-60-UR-8100A | C | M | 4.4:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA , AND SMALL CUTS .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)this is general comment for SRN 302 | Originated |  | PS5-60-01 - Power Generation Package A
PL-000817 | PS5-60-UR-8100A | C | M | 4.6:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA , AND SMALL CUTS .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)-STRAIGHT LENGTH L1250mm DIA 450/650 EXHAUST LINE | Originated |  | PS5-60-01 - Power Generation Package A
PL-000818 | PS5-60-UR-8100A | C | M | 4.7:FOUND MINOR SCRATCHES, GAPS ON THE OUTER COVER THAT COULD ALLOW WATER ENTRY INTO THE INSULATED AREA .(Gaps not properly filled/sealed, Partially used mastic to seal which have not working)-ADJUSTABLE LENGTH L6000-6250mm DIA 950/1150 EXHAUST LINE | Originated |  | PS5-60-01 - Power Generation Package A
PL-000819 | PS5-60-UR-8100A | B | M | 4.8:NO PROPER PACKING LIST/NOTE AVAILABLE FOR SRN 303 FASTNERS. FOUND BOLT- M12*60=3500, M16*80=450, M30*80=670, M36*80=690, M36*90=60 NUT- M36=750, M12=3500, M16=450 ,, M30=30 WASHER- M36=1500, M13=7000 ,M16=900, M31=700 | Originated |  | PS5-60-01 - Power Generation Package A
PL-000820 | PS5-60-UR-8100A | C | M | 4.9:FOUND SOME EXTRA MATERIAL IN SRN 303 (Not mentioned in PL) SILICON NEUTRA- 72 PCS. RIVETS -6 BOX PROETEX PTFE TAPE - 15 PCS ROPE SEAL - 1 PACKET | Originated |  | PS5-60-01 - Power Generation Package A
PL-000821 | PS5-60-UR-8100A | B | M | 4.10:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100A | Originated |  | PS5-60-01 - Power Generation Package A
PL-000822 | PS5-60-UR-8100C | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100C | Originated |  | PS5-60-07 - Power Generation Package C
PL-000823 | PS5-60-UR-8100D | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100D | Originated |  | PS5-60-10 - Power Generation Package D
PL-000824 | PS5-60-UR-8100E | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100E | Originated |  | PS5-60-13 - Power Generation Package E
PL-000825 | PS5-60-UR-8100G | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100G | Originated |  | PS5-60-19 - Power Generation Package G
PL-000826 | PS5-60-UR-8100F | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100F | Originated |  | PS5-60-16 - Power Generation Package F
PL-000827 | PS5-60-UR-8100B | B | M | 4:SOME BALL VALVES AND OPENINGS ARE IMPROPERLY PLUGGED IN COMPACT UNIT PS5-60-UO-81100B | Originated |  | PS5-60-04 - Power Generation Package B
PL-000828 | PS5-60-UR-8100G | B | E | 4.1: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41700A/B) | Originated |  | PS5-60-19 - Power Generation Package G
PL-000829 | PS5-60-UR-8100A | B | M | 4.11:THERE IS NO PROPER PACKING LIST, AND ACCORDING TO THE COLLI LIST, 1 REGULATING RING IS MISSING. ONLY 5 RINGS WERE FOUND ACROSS ALL THE BOXES.-SHIPPED LOOSE ITEM SRN 311 | Originated |  | PS5-60-01 - Power Generation Package A
PL-000830 | PS5-60-UR-8100A | B | M | 4.12:NO PROPER PACKING LIST AVAILABLE- SRN 311 CAPITAL SPARES | Originated |  | PS5-60-01 - Power Generation Package A
PL-000831 | PS5-60-UR-8100A | B | M | 4.13:THE DRYER COVER IS DAMAGED- INSTRUMENTATION AIR STATION PS5-60-UA-5200 | Originated |  | PS5-60-01 - Power Generation Package A
PL-000832 | PS5-60-UR-8100A | A | M | 4.14:2 OF THE FLEXIBLE HOSES ARE DAMAGED AND NEEDS REPLACEMENT-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | Closed | 2026-07-04 | PS5-60-01 - Power Generation Package A
PL-000833 | PS5-60-UR-8100A | A | M | 4.15:THE SPRINGS HAVE BEEN DISPLACED FROM THE BOTTOM OF THE EQUIPMENT.-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | Closed | 2026-07-04 | PS5-60-01 - Power Generation Package A
PL-000834 | PS5-60-UR-8100A | B | M | 4.16:THE COMPRESSOR COVER GUIDE IS DAMAGED-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | Originated |  | PS5-60-01 - Power Generation Package A
PL-000835 | PS5-60-UR-8100A | B | M | 4.17:THE PRV 5206 OUTLET IS NOT PLUGGED.-INSTRUMENTATION AIR STATION PS5-60-UA-5200 | Originated |  | PS5-60-01 - Power Generation Package A
PL-000836 | PS5-60-UR-8100A | B | M | 4.18: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41100A/B) | Originated |  | PS5-60-01 - Power Generation Package A
PL-000837 | PS5-60-UR-8100C | B | E | 4.1: THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41300A/B) | Originated |  | PS5-60-07 - Power Generation Package C
PL-000838 | PS5-60-UR-8100D | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41400A/B) | Originated |  | PS5-60-10 - Power Generation Package D
PL-000839 | PS5-60-UR-8100E | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41500A/B) | Originated |  | PS5-60-13 - Power Generation Package E
PL-000840 | PS5-60-UR-8100F | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41600A/B) | Originated |  | PS5-60-16 - Power Generation Package F
PL-000841 | PS5-60-UR-8100B | B | E | 4.1:THE MAGNETIC FLOAT SWITCH OPENING IS NOT PROPERLY PLUGGED.(JACKET WATER EXPANSION TANK & SCAC EXPANSION TANK PS5-60-TX-41200A/B) | Originated |  | PS5-60-04 - Power Generation Package B
PL-000842 | PS5-60-UR-8100A | C | M | 4.19:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | Originated |  | PS5-60-01 - Power Generation Package A
PL-000843 | PS5-60-UR-8100C | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | Originated |  | PS5-60-07 - Power Generation Package C
PL-000844 | PS5-60-UR-8100D | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | Originated |  | PS5-60-10 - Power Generation Package D
PL-000845 | PS5-60-UR-8100E | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | Originated |  | PS5-60-13 - Power Generation Package E
PL-000846 | PS5-60-UR-8100G | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | Originated |  | PS5-60-19 - Power Generation Package G
PL-000847 | PS5-60-UR-8100F | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | Originated |  | PS5-60-16 - Power Generation Package F
PL-000848 | PS5-60-UR-8100B | C | M | 4.2:THE INSULATION CLADDING IS NOT PROPERLY SEALED-450NB Y PIECE | Originated |  | PS5-60-04 - Power Generation Package B
PL-000849 | PS5-60-UR-8100G | C | M | 4.3:THE Y-PIECE IS BENT AT A CERTAIN POINT. | Originated |  | PS5-60-19 - Power Generation Package G
PL-000850 | PS5-60-UR-8100A | C | M | 4.20:Found Electric compressor motor solenoid valve power and earthing cable damaged for Instrumentation air station package (PS5-60-UA-5200). | Originated |  | PS5-60-01 - Power Generation Package A
PL-000851 | PS5-60-UR-8100A | C | M | 4.21:All CO Control panel tag no need to be corrected as per building layout drawing- SRN 311 CO CONTROL CABINET | Originated |  | PS5-60-01 - Power Generation Package A
PL-000852 | PS5-60-UR-8100A | C | M | 4.22:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | Originated |  | PS5-60-01 - Power Generation Package A
PL-000853 | PS5-60-UR-8100C | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | Originated |  | PS5-60-07 - Power Generation Package C
PL-000854 | PS5-60-UR-8100D | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | Originated |  | PS5-60-10 - Power Generation Package D
PL-000855 | PS5-60-UR-8100E | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | Originated |  | PS5-60-13 - Power Generation Package E
PL-000856 | PS5-60-UR-8100G | C | M | 4.4:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | Originated |  | PS5-60-19 - Power Generation Package G
PL-000857 | PS5-60-UR-8100F | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | Originated |  | PS5-60-16 - Power Generation Package F
PL-000858 | PS5-60-UR-8100B | C | M | 4.3:ALL THE SILENCERS HAVE PS4 TAGS, WHILE THE TARPAULINS HAVE PS5 TAGS, INDICATING THEY HAVE BEEN EXCHANGED. | Originated |  | PS5-60-04 - Power Generation Package B
PL-000859 | PS5-60-UR-8100A | B | M | 4.23:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100A | Closed | 2026-07-09 | PS5-60-01 - Power Generation Package A
PL-000860 | PS5-60-UR-8100C | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100C | Completed |  | PS5-60-07 - Power Generation Package C
PL-000861 | PS5-60-UR-8100D | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100D | Closed | 2026-07-09 | PS5-60-10 - Power Generation Package D
PL-000862 | PS5-60-UR-8100E | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100E | Closed | 2026-07-09 | PS5-60-13 - Power Generation Package E
PL-000863 | PS5-60-UR-8100G | B | M | 4.5:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100G | Closed | 2026-07-09 | PS5-60-19 - Power Generation Package G
PL-000864 | PS5-60-UR-8100F | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100F | Originated |  | PS5-60-16 - Power Generation Package F
PL-000865 | PS5-60-UR-8100B | B | M | 4.4:THE AIR STARTING RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED.-PS5-60-VA-5100B | Originated |  | PS5-60-04 - Power Generation Package B
PL-000866 | PS5-60-UR-8100E | A | M | 4.5:THE AIR STARTING RECEIVER PS5-60-VA-5100E SOLENOID VALVE IS DISCONNECTED AND LYING ON THE GROUND. | Originated |  | PS5-60-13 - Power Generation Package E
PL-000867 | PS5-60-UR-8100F | C | M | 4.5:THE MATERIAL OF THE VESSEL IS UNEVEN AND IRREGULAR.(AIR STARTING RECEIVER PS5-60-VA-5100F) | Originated |  | PS5-60-16 - Power Generation Package F
PL-000868 | PS5-60-UR-8100A | B | M | 4.24:THE AIR RECEIVER HAS MULTIPLE OPENINGS THAT ARE NOT PROPERLY PLUGGED(PS5-60-VA-5200) | Originated |  | PS5-60-01 - Power Generation Package A
PL-000870 | PS5-28-UZ-8100 | B | M | 4:FOUND TYRES WITH BUMPS(H150 PUMP SET +MOTOR+ MOBILE TROLLEY) | Originated |  | PS5-28-10 - Oil Skimmer Package
PL-000871 | PS5-28-UZ-8100 | B | M | 4.1:THE H150 PUMPSET HAS OPENINGS THAT ARE NOT PROPERLY PLUGGED. | Originated |  | PS5-28-10 - Oil Skimmer Package
PL-000872 | PS5-28-UZ-8100 | C | M | 4.2:THE TERMINAL BOX EXHIBITS PAINT DAMAGE.(H150 PUMP SET +MOTOR+ MOBILE TROLLEY) | Originated |  | PS5-28-10 - Oil Skimmer Package
PL-000873 | PS5-28-UZ-8100 | B | M | 4.3:START-UP SPARES ARE NOT AVAILABLE. | Originated |  | PS5-28-10 - Oil Skimmer Package
PL-000874 | PS5-28-UZ-8100 | B | M | 4.4:OVERAGE-FOUND INDUSTRIAL PLUG & SOCKET- OUTLETS DECONTACTOR AND BOXES,CLOSING MECHANISM & SOCKET DXN6. | Originated |  | PS5-28-10 - Oil Skimmer Package
PL-001011 | PS5-60-IH-0002 | C | E | Panel Tag Number need to be provided for PS5-60-IH-0002/1&2 | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-001012 | PS5-60-IE-0002A | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002A | Originated |  | PS5-60-01 - Power Generation Package A
PL-001013 | PS5-60-IE-0002B | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002B | Originated |  | PS5-60-04 - Power Generation Package B
PL-001014 | PS5-60-IE-0002C | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002C | Originated |  | PS5-60-07 - Power Generation Package C
PL-001015 | PS5-60-IE-0002D | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002D | Originated |  | PS5-60-10 - Power Generation Package D
PL-001016 | PS5-60-IE-0002E | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002E | Originated |  | PS5-60-13 - Power Generation Package E
PL-001017 | PS5-60-IE-0002F | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002F | Originated |  | PS5-60-16 - Power Generation Package F
PL-001018 | PS5-60-IE-0002G | B | E | Panel key's need to be provided for Panel PS5-60-IE-0002G | Originated |  | PS5-60-19 - Power Generation Package G
PL-001019 | PS5-60-IE-0004 | B | E | Panel key need to be provided for PS5-60-IE-0004 | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-001050 | PS5-60-IH-0001B | B | E | Damaged bottom plinth needs to be fixed properly for PS5-60-IH-0001B/3&4 | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-001051 | PS5-60-IH-0001B | B | E | Panel C4 compartment door not open need to be rectified for PS5-60-IH-0001B/3&4 | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-001052 | PS5-60-IE-0004 | A | E | Workstation desktop package inside mouse missing and need to be provided (4CE251CSBC) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-001228 | PS5-28-VSP-1300A | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | Originated |  | PS5-28-13 - Seal Oil Drain Drum & Pump A
PL-001229 | PS5-28-VSP-1300B | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | Originated |  | PS5-28-14 - Seal Oil Drain Drum & Pump B
PL-001230 | PS5-28-VSP-1300C | C | M | 4:FOUR JACKING BOLTS ARE FOUND MISSING FROM THE SEAL OIL DRAIN DRUM | Originated |  | PS5-28-15 - Seal Oil Drain Drum & Pump C
PL-001231 | PS5-25-PA-3100A | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001232 | PS5-25-PA-3100A | C | M | 4.1:THE PLUGS FOR GATE VALVE 130 AND 134 ARE MISSING | Completed |  | PS5-25-02 - Crude Oil Export Pump A
PL-001233 | PS5-25-PA-3100A | B | M | 4.2:PSV 104 CALIBRATION SEAL WIRE IS BROKEN | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001234 | PS5-25-PA-3100A | C | M | 4.3:MOTOR TERMINAL BOX SUPPORT IS MISSING | Closed | 2025-06-24 | PS5-25-02 - Crude Oil Export Pump A
PL-001235 | PS5-25-PA-3100A | A | M | 4.4:FLANGE CONNECTION TO FO 103 – NUT BOLT MISSING | Completed |  | PS5-25-02 - Crude Oil Export Pump A
PL-001236 | PS5-25-PA-3100A | C | E | 4.5:PS5-25-TE-8103A TRAFFOLYTE TAG IS DAMAGED | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001237 | PS5-25-PA-3100A | C | M | 4.6:SOME OF THE BOLTS IN THE PUMP BEARING HOUSING ARE RUSTED | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001238 | PS5-25-PA-3100A | C | E | 4.7:JB KEYS NOT FOUND | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001239 | PS5-25-PA-3100A | B | E | 4.8:TIT 3012 SENSOR NOT PROPERLY SECURE, THE SENSOR IS EXPOSED , NEED TO BE INSTALLED | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001240 | PS5-25-PA-3100A | A | E | 4.9:EARTHING POINTS MISSING GROUNDING CONNECTIONS | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001241 | PS5-25-PA-3100A | C | E | 4.10:CABLE TAG FOR ORANGE CABLE MISSING(PS5-79-IP-0001) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001242 | PS5-25-PA-3100A | B | M | 4.11:CANOPY & CANOPY SUPPORT MISSING(PS5-25-LIT-8102A) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001243 | PS5-25-PA-3100A | B | M | 4.12:CANOPY MISSING(PS5-25-PIT-8102A) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001244 | PS5-25-PA-3100A | C | E | 4.13:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003 ) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001245 | PS5-25-PA-3100A | C | M | 4.14:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB(PS5-25-BI-1801A) | Completed |  | PS5-25-02 - Crude Oil Export Pump A
PL-001246 | PS5-25-PA-3100B | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001247 | PS5-25-PA-3100B | A | M | 4.1:THE PIPE FLANGE TO THE LUBE OIL COOLER IS MISSING 4 NUTS, BOLTS, AND A GASKET | Completed |  | PS5-25-03 - Crude Oil Export Pump B
PL-001248 | PS5-25-PA-3100B | C | M | 4.2:THE MOTOR DM 102 IS NOT SECURED AND IS SHAKING , 2 SCREWS ARE MISSING | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001249 | PS5-25-PA-3100B | C | M | 4.3:SOME OF THE BOLTS IN THE PUMP BEARING HOUSING ARE RUSTED | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001250 | PS5-25-PA-3100B | C | M | 4.4:THE PLUGS FOR GATE VALVE 132 AND 133 ARE MISSING | Completed |  | PS5-25-03 - Crude Oil Export Pump B
PL-001251 | PS5-25-PA-3100B | C | M | 4.5:PSV STUD BOLT IS MISSING | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001252 | PS5-25-PA-3100B | C | M | 4.6:MOTOR TERMINAL BOX SUPPORT IS MISSING | Closed | 2025-06-24 | PS5-25-03 - Crude Oil Export Pump B
PL-001253 | PS5-25-PA-3100B | B | E | 4.7:TIT 3012 SENSOR NOT PROPERLY SECURE, THE SENSOR IS EXPOSED , NEED TO BE INSTALLED | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001255 | PS5-25-PA-3100B | C | E | 4.8:JB KEYS NOT FOUND | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001256 | PS5-25-PA-3100B | A | M | 4.9:THE TEMP GAUGE, PROVIDED AS A LOOSE ITEM, HAS NO LOCK NUT | Closed | 2026-07-04 | PS5-25-03 - Crude Oil Export Pump B
PL-001257 | PS5-25-PA-3100B | A | E | 4.10:EARTHING POINTS MISSING GROUNDING CONNECTIONS | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001258 | PS5-25-PA-3100B | C | E | 4.11:CABLE TAG FOR ORANGE CABLE MISSING (PS5-79-IP-0002) | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001259 | PS5-25-PA-3100B | B | M | 4.12:CANOPY & CANOPY SUPPORT MISSING (PS5-25-LIT-8102B) | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001260 | PS5-25-PA-3100B | B | M | 4.13:CANOPY MISSING (PS5-25-PIT-8102B) | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001261 | PS5-25-PA-3100B | C | E | 4.14:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003) | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001262 | PS5-25-PA-3100B | C | M | 4.15:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB .(PS5-25-BI-1801B) | Completed |  | PS5-25-03 - Crude Oil Export Pump B
PL-001263 | PS5-25-PA-3100C | B | M | 4:IN THE PACKING LIST, THE M32 CABLE GLAND AND SHROUD SHOULD BE 3, BUT WE RECEIVED ONLY 2 | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001264 | PS5-25-PA-3100C | C | M | 4.1:PSV STUD BOLT IS MISSING | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001265 | PS5-25-PA-3100C | B | E | 4.2:TIT 3012 SENSOR IS SLIGHTLY BEND AND NOT PROPERLY SECURED, THE SENSOR IS EXPOSED . NEED TO BE INSTALLED | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001266 | PS5-25-PA-3100C | C | E | 4.3:JB KEYS NOT FOUND | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001267 | PS5-25-PA-3100C | A | M | 4.4:THE TEMP GAUGE, PROVIDED AS A LOOSE ITEM, HAS NO LOCK NUT | Closed | 2026-07-04 | PS5-25-04 - Crude Oil Export Pump C
PL-001268 | PS5-25-PA-3100C | C | M | 4.5:THE PLUGS FOR GATE VALVE 132 IS MISSING | Completed |  | PS5-25-04 - Crude Oil Export Pump C
PL-001269 | PS5-25-PA-3100C | A | E | 4.6:EARTHING POINTS MISSING GROUNDING CONNECTIONS | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001270 | PS5-25-PA-3100C | C | E | 4.7:CABLE TAG FOR ORANGE CABLE MISSING (PS5-79-IP-0003) | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001271 | PS5-25-PA-3100C | B | M | 4.8:CANOPY & CANOPY SUPPORT MISSING (PS5-25-LIT-8102C) | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001272 | PS5-25-PA-3100C | B | M | 4.9:CANOPY MISSING (PS5-25-PIT-8102C) | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001273 | PS5-25-PA-3100C | C | E | 4.10:CABLE TAG MISSING FOR ALL IP DEVICES (PS5-79-IP-9902/9003/9004/0003 ) | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001274 | PS5-25-PA-3100C | C | M | 4.11:JB CANOPY MISSING (PS5-25-BI-1274C) | Completed |  | PS5-25-04 - Crude Oil Export Pump C
PL-001275 | PS5-25-PA-3100C | C | M | 4.12:CANOPY NOT PROVIDED FOR JB AS ELECTRONIC COMPONENTS ARE PRESENT INSIDE THE JB. (PS5-25-BI-1801C) | Completed |  | PS5-25-04 - Crude Oil Export Pump C
PL-001276 | PS5-25-PA-3100C | C | M | 4.13:MOTOR TERMINAL BOX SUPPORT IS MISSING | Closed | 2025-06-24 | PS5-25-04 - Crude Oil Export Pump C
PL-001303 | PS5-25-UJ-6100 | A | M | 4:As per the packing list, 3 PGs were listed, but only 2 were received. One PG is missing. | Closed | 2026-07-04 | PS5-25-02 - Crude Oil Export Pump A
PL-001304 | PS5-25-UJ-6100 | B | M | 4.1:Received 2 pressure gauges, both of which are leaking from the dial. Replacement or refilling by the vendor is required | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001305 | PS5-25-UJ-6100 | B | M | 4.2: Missing as per packing list ( 60. Rubber metal cushion, 65.Stud, 70.Wear insert, 80. Hexagon nut not found) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001306 | PS5-25-UJ-6100 | C | M | 4.3:Overage material (control gear unit received which is not showing in PL) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001312 | PS5-71-HE-2400A | C | M | 4:FOUND 6 nos CABLE GLANDS 4 nos RTJ GASKETS WHICH ARE NOT SHOWING IN PACKING LIST , 2 nos SLIDING PLATE (OVERAGE) | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001313 | PS5-71-HE-2400A | B | M | 4.1:4NOS. GASKETS MISSING (AS PER PL 8NOS.) | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001314 | PS5-71-HE-2400A | B | M | 4.2:6NOS. BOLTS MISSING (AS PER PL 12NOS.) | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001315 | PS5-71-HE-2400A | B | M | 4.3:12 NOS. NUTS MISSING (AS PER PL 24NOS.) | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001316 | PS5-71-HE-2400A | B | M | 4.4:12 NOS. WASHERS MISSING (AS PER PL 24NOS.) | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001317 | PS5-71-HE-2400A | C | E | 4.5:ELECTRICAL CABLE ENTRIES WERE NOT PLUGGED | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001318 | PS5-71-HE-2400A | B | M | 4.6:4 EACH BOLTS MISSING ON 2 FLANGES | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001319 | PS5-71-HE-2400B | B | M | 4:TOTAL 8 BOLTS MISSING ON 2 FLANGES | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001320 | PS5-53-PA-3100A | C | M | 4:PAINT DAMAGE IN THE MOTOR TERMINAL BOX | Originated |  | PS5-53-02 - Water Distribution Pump A/B
PL-001321 | PS5-53-PA-3100B | C | M | 4:PAINT DAMAGE IN THE MOTOR TERMINAL BOX | Originated |  | PS5-53-02 - Water Distribution Pump A/B
PL-001322 | PS5-28-PA-3300 | C | M | 4:We received two vertical pumps, but the plugs are not available | Closed | 2025-07-15 | PS5-28-06 - Relief Drum and Pump
PL-001323 | PS5-28-PA-3400 | C | M | 4:We received two vertical pumps, but the plugs are not available. | Closed | 2025-07-15 | PS5-28-03 - Closed Drain Drum and Pump 01
PL-001324 | PS5-25-ZS-1201 | B | M | 4:PIG SIGNALLER FLANGE SURFACE IS RUSTED | Originated |  | PS5-25-07 - Export Pipeline Pig Launcher
PL-001328 | PS5-71-PA-3500A | B | M | 4:Oil leakage detected from the pump (PS5-71-PA-3500A) | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-001329 | PS5-71-PA-3500B | B | M | 4:Oil leakage detected from the pump (PS5-71-PA-3500B) | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-001330 | PS5-28-PA-3700A | B | M | 4:Oil leakage detected from the pump (PS5-28-PA-3700A) | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-001331 | PS5-28-PA-3700A | C | M | 4.1:Pump body flanges are rusted (PS5-28-PA-3700A) | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-001332 | PS5-28-PA-3700B | B | M | 4:Oil leakage detected from the pump (PS5-28-PA-3700B) | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-001333 | PS5-53-TR-4100 | C | M | 4:(PACKAGE NO :6) 10000 X 2000= 2 pcs OVERAGE | Originated |  | PS5-53-01 - Utility Water / Storage Tank
PL-001334 | PS5-53-TR-4100 | C | M | 4.1:(PACKAGE NO :10), 120X120X8 = 2000MM LENGTH 1 pcs OVERAGE | Originated |  | PS5-53-01 - Utility Water / Storage Tank
PL-001335 | PS5-53-TR-4100 | C | M | 4.2:(PACKAGE: 6 & 7 ) 2 PLATE DAMAGE | Completed |  | PS5-53-01 - Utility Water / Storage Tank
PL-001336 | PS5-53-TR-4100 | C | M | 4.3:(PACKAGE:14 ) 2 ROOF PLATE DAMAGE | Completed |  | PS5-53-01 - Utility Water / Storage Tank
PL-001337 | PS5-53-TR-4100 | C | M | 4.4:(PACKAGE:15 ) 1 ROOF PLATE DAMAGE | Completed |  | PS5-53-01 - Utility Water / Storage Tank
PL-001338 | PS5-53-TR-4100 | B | M | 4.5:(PACKAGE:10) CURB ANGLE FOUND BEND | Closed | 2026-07-09 | PS5-53-01 - Utility Water / Storage Tank
PL-001339 | PS5-53-TR-4100 | A | M | 4.6:THE MG TANK ANODE SHOULD BE SUPPLIED WITH U BOLT, MOUNTING BRACKET, DOUBLE NUT, FLAT WASHER, AND LOCK WASHER; HOWEVER, WE ONLY RECEIVED THE ANODES.(CP SYSTEM MATERIAL , SRN-517) | Closed | 2026-07-04 | PS5-53-01 - Utility Water / Storage Tank
PL-001397 | PS5-78-JC-9100A | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED | Closed | 07-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001398 | PS5-78-JC-9100A | C | M | 4.1:HOOK IS RUSTED | Closed | 07-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001407 | PS5-78-JC-9100A | B | E | 4.2:ELECTRICAL PANEL BOARD IS DAMAGED | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001408 | PS5-78-JC-9100A | B | M | 4.3:2 BOLTS MISSING IN PANNEL AT TROLLEY BUMBER | Closed | 07-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001409 | PS5-78-JC-9100A | B | E | 4.4: GROUNTING / EARTHING POINT NOT PROVIDED FOR THE PANNEL BOXES | Closed | 07-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001410 | PS5-78-JC-9100A | B | E | 4.5:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001411 | PS5-78-JC-9100A | C | M | 4.6:TAG NUMBERS OF ALL THE PANEL BOX/JBS NEED TO BE FIXED PROPERLY(WITH REVETS OR SCREWS) | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001412 | PS5-78-JC-9100A | A | M | 4.7: PENDANT TRACK IS BEND | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001413 | PS5-78-JC-9100A | B | M | 4.8:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER. | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001414 | PS5-78-JC-9100A | B | M | 4.9:PLATFORM DAMAGED (PAINT AND METAL DAMAGES, SEVERE BENDS ON THE PLATFORM) | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001415 | PS5-78-JC-9100A | B | M | 4.10:THE HANDRAIL HAS PAINT DAMAGE AND IS SEVERELY BENT DUE TO MISHANDLING | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001416 | PS5-78-JC-9100A | B | M | 4.11:DOOR LOCK HANDLE IS MISSING | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001417 | PS5-78-JC-9100A | C | M | 4.12:HAND RAIL PAINT DAMAGE | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001418 | PS5-78-JC-9100A | C | M | 4.13:HANDRAIL BOLT NUT MISSING (6 NOS) | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001419 | PS5-78-JC-9100A | C | M | 4.14:CABLE TROLLEYS UNIT IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001420 | PS5-78-JC-9100A | A | M | 4.15:DOOR FIXING SCREWS ARE MISSING | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001421 | PS5-78-JC-9100A | A | M | 4.16:C HANGERS NOT RECEIVED | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001422 | PS5-78-JC-9100A | C | M | 4.17:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001425 | PS5-78-JC-9100B | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001426 | PS5-78-JC-9100B | C | M | 4.1:PS5-78-DE-352008 HOISTING UNIT PAINT IS DAMAGED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001427 | PS5-78-JC-9100B | B | E | 4.2:GROUNTING / EARTHING PONINT NOT PROVIDED FOR THE PANNEL | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001428 | PS5-78-JC-9100B | B | E | 4.3:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001429 | PS5-78-JC-9100B | C | E | 4.4:TAG NUMBERS OF ALL THE PANEL BOX/JBS NEED TO BE FIXED PROPERLY | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001430 | PS5-78-JC-9100B | B | M | 4.5:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001431 | PS5-78-JC-9100B | C | M | 4.6:HAND RAIL AND PLATFORM PAINT IS DAMAGED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001432 | PS5-78-JC-9100B | B | M | 4.7:DOOR LOCK MISSING | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001433 | PS5-78-JC-9100B | B | M | 4.8:HAND RAIL IS SEVERELY BEND | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001435 | PS5-78-JC-9100B | A | M | 4.9:14 C HANGERS NOT RECEIVED | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001436 | PS5-78-JC-9100B | C | M | 4.10:CABLE TROLLEY UNIT IS RUSTED | Completed |  | PS5-78-01 - Lifting and handling equipment
PL-001438 | PS5-78-JC-9100B | C | M | 4.11:SWITCH STOP UNIT PAINT IS DAMAGED | Completed |  | PS5-78-01 - Lifting and handling equipment
PL-001447 | PS5-78-JC-9100B | C | M | 4.12:6 HAND RAIL BOLTS MISSING | Completed |  | PS5-78-01 - Lifting and handling equipment
PL-001448 | PS5-78-JC-9100B | A | M | 4.13:DOOR FIXING SCREWS ARE MISSING | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001449 | PS5-78-JC-9100B | B | M | 4.14:2 BOLTS MISSING IN PANNEL AT TROLLEY BUMBER | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001450 | PS5-78-JC-9100B | C | M | 4.15:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001451 | PS5-78-JC-9100C | C | M | 4:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED. | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001452 | PS5-78-JC-9100C | C | M | 4.1:HOOK BLOCK AREA IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001453 | PS5-78-JC-9100C | C | M | 4.2:HOISTING UNIT 2 LOCK NUTS ARE RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001454 | PS5-78-JC-9100C | B | E | 4.3: GROUNTING / EARTHING POINT IS NOT PROVIDED FOR THE PANNEL | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001455 | PS5-78-JC-9100C | B | E | 4.4:CABLE FERRULES NEED TO BE PROVIDED FOR ALL PANNEL BOXES | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001456 | PS5-78-JC-9100C | C | E | 4.5:TAG NUMBERS OF ALL THE PANEL BOX/JB NEED TO BE FIXED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001457 | PS5-78-JC-9100C | C | M | 4.6:WARNING STICKER IS DAMAGE | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001458 | PS5-78-JC-9100C | B | M | 4.7:2 BOLTS MISSING IN THE PANNEL AT TROLLEY BUMBER | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001459 | PS5-78-JC-9100C | A | M | 4.8:TOOL MISSING | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001460 | PS5-78-JC-9100C | B | M | 4.9:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON GIRDER | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001461 | PS5-78-JC-9100C | A | M | 4.10:PENDANT TRACK IS BEND | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001462 | PS5-78-JC-9100C | B | M | 4.11:3 HAND RAIL SEVERELY BEND DUE TO MISHANDLING. | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001463 | PS5-78-JC-9100C | C | M | 4.12:HAND RAIL & PLATFORM PAINT IS DAMAGED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001464 | PS5-78-JC-9100C | C | M | 4.13:6 HANDRAIL NUT BOLT MISSING | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001465 | PS5-78-JC-9100C | A | M | 4.14:9 DOOR FIXING SCREWS ARE MISSING | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001466 | PS5-78-JC-9100C | A | M | 4.15:14 C- HANGERS NOT RECEIVED | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001467 | PS5-78-JC-9100C | C | M | 4.16:CABLE TROLLEY UNIT IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001468 | PS5-78-JC-9100C | C | M | 4.17:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDERE IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001469 | PS5-78-JC-9100D | B | M | The Hoist fan cover/ support found damage and need to be replaced-Damage during transportation | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001470 | PS5-78-JC-9100D | B | M | The brake resistor found damage and need to be replaced-Damage during transportation | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001471 | PS5-78-JC-9100D | C | M | 4.2:HOISTING UNIT IS NOT PROPERLY PACKED. | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001472 | PS5-78-JC-9100D | C | M | 4.3:ROPE DRUM (GROOVE OF THE STEEL ROPE) OF THE HOIST IS RUSTED. | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001473 | PS5-78-JC-9100D | B | M | 4.4:2 BOLTS MISSING IN THE PANNEL OF THE TROLLEY BUMBER | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001474 | PS5-78-JC-9100D | B | E | 4.5:GROUNTING/ EARTHING POINT NOT PROVIDED FOR THE PANEL | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001475 | PS5-78-JC-9100D | B | E | 4.6:CABLE FERRULES NEED TO BE PROVIDED FOR ALL THE PANNEL BOXES | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-001476 | PS5-78-JC-9100D | C | E | 4.7:TAG NUMBERS OF ALL THE PANEL BOX/JBs NEED TO BE FIXED PROPERLY. | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001477 | PS5-78-JC-9100D | B | M | 4.8:PAINT DAMAGE / PARENT METAL DAMAGE FOUND ON THE GIRDER | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001478 | PS5-78-JC-9100D | A | M | 4.9:PENDANT TRACK IS DAMAGED AND BEND. | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001479 | PS5-78-JC-9100D | C | M | 4.10:HAND RAIL IS SEVERELY BEND DUE TO MISHANDLING | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001480 | PS5-78-JC-9100D | C | M | 4.11:HAND RAIL AND PLATFORM PAINT IS DAMAGED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001481 | PS5-78-JC-9100D | B | M | 4.12:DOOR LOCK HANDLE MISSING | Completed |  | PS5-78-01 - Lifting and handling equipment
PL-001482 | PS5-78-JC-9100D | A | M | 4.13:ONE OVERAGE BOX OF CARBOLINE FIREPROOF COATING IS LEAKING | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001483 | PS5-78-JC-9100D | A | M | 4.14:9 DOOR FIXING SCREWS ARE MISSING | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001484 | PS5-78-JC-9100D | C | M | 4.15:6 HANDRAIL NUT BOLT MISSING | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001485 | PS5-78-JC-9100D | A | M | 4.16:14 C HANGERS NOT RECEIVED | Closed | 04-Mar-26 | PS5-78-01 - Lifting and handling equipment
PL-001486 | PS5-78-JC-9100D | C | M | 4.17:CABLE TROLLEYS UNIT IS RUSTED | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001487 | PS5-78-JC-9100D | C | M | 4.18:THE TRACK ON TOP OF THE OVER HEAD CRANE GIRDER IS RUST | Closed | 02-May-26 | PS5-78-01 - Lifting and handling equipment
PL-001488 | PS5-60-PA-3300 | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-001490 | PS5-05-UR-8100 | A | M | DUE TO THE MISALIGNMENT OF PENETRATIONS BETWEEN EDG & HYDRAULIC CABIN FIRE FIGHTING SYSTEM TUBING CANNOT BE CONNECTED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-001491 | PS5-05-UR-8100 | A | M | DUE TO THE MISALIGNMENT OF PENETRATIONS BETWEEN EDG & MIST CABIN FIRE FIGHTING SYSTEM TUBING CANNOT BE CONNECTED | Closed | 2026-02-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-001547 | PS5-71-PA-3500A | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-001548 | PS5-71-PA-3500B | A | M | CAT LUBE OIL 15W40, USED FOR PRESERVATION, MUST BE DRAINED AND FLUSHED BEFORE COMMISSIONING. | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-001566 | PS5-53-PA-3100A | A | M | USE CAT 15W40 LUBE OIL FOR PRESERVATION, FLUSH AND USE THE PROPER LUBE OIL. | Originated |  | PS5-53-02 - Water Distribution Pump A/B
PL-001610 | PS5-60-EA-2400A | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | Closed | 2026-07-04 | PS5-60-73 - Engine D Cooling system
PL-001614 | PS5-60-EA-2400B | C | M | 4:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-73 - Engine D Cooling system
PL-001615 | PS5-60-EA-2400B | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-73 - Engine D Cooling system
PL-001616 | PS5-60-EA-2400B | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-73 - Engine D Cooling system
PL-001617 | PS5-60-EA-2200A | C | M | 4:END COVER OF THE HEADDER(CLADDING) DAMAGE (MAY BE DURING TRANSPORTATION) | Originated |  | PS5-60-71 - Engine B Cooling system
PL-001618 | PS5-60-EA-2200A | A | M | 4.1:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | Closed | 2026-07-04 | PS5-60-71 - Engine B Cooling system
PL-001619 | PS5-60-EA-2200A | C | M | 4.2:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-71 - Engine B Cooling system
PL-001620 | PS5-60-EA-2200A | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-71 - Engine B Cooling system
PL-001622 | PS5-60-EA-2200A | A | M | 4.5:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-71 - Engine B Cooling system
PL-001623 | PS5-60-EA-2200B | C | M | 4:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-71 - Engine B Cooling system
PL-001624 | PS5-60-EA-2500A | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | Closed | 2026-07-04 | PS5-60-74 - Engine E Cooling system
PL-001625 | PS5-60-EA-2100A | C | M | 4:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-70 - Engine A Cooling system
PL-001626 | PS5-60-EA-2100A | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-70 - Engine A Cooling system
PL-001627 | PS5-60-EA-2100A | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-70 - Engine A Cooling system
PL-001628 | PS5-60-EA-2100B | C | M | 4:VALVE HANDLE COATING/COVER MISSING | Originated |  | PS5-60-70 - Engine A Cooling system
PL-001629 | PS5-60-EA-2100B | C | M | 4.1:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-70 - Engine A Cooling system
PL-001630 | PS5-60-EA-2100B | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-70 - Engine A Cooling system
PL-001631 | PS5-60-EA-2100B | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-70 - Engine A Cooling system
PL-001632 | PS5-60-EA-2400A | C | M | 4.1:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-73 - Engine D Cooling system
PL-001633 | PS5-60-EA-2400A | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-73 - Engine D Cooling system
PL-001634 | PS5-60-EA-2400A | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-73 - Engine D Cooling system
PL-001641 | PS5-60-EA-2200B | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-71 - Engine B Cooling system
PL-001642 | PS5-60-EA-2200B | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-71 - Engine B Cooling system
PL-001643 | PS5-60-EA-2500A | C | M | 4.1:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-001645 | PS5-60-EA-2500A | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-74 - Engine E Cooling system
PL-001646 | PS5-60-EA-2500A | A | M | 4.4:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-74 - Engine E Cooling system
PL-001647 | PS5-60-EA-2500B | A | M | 4:HEADDER AND BRANCH GOT SEVERE DAMAGE (May be during transportation) AND NEED TO BE RECTIFIED | Closed | 2026-07-04 | PS5-60-74 - Engine E Cooling system
PL-001648 | PS5-60-EA-2500B | C | M | 4.1:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-001650 | PS5-60-EA-2500B | C | M | 4.2:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-74 - Engine E Cooling system
PL-001651 | PS5-60-EA-2500B | A | M | 4.3:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-74 - Engine E Cooling system
PL-001652 | PS5-60-EA-2600A | A | M | 4:NOZZLE/BRANCH ZAGGED DUE TO IMPROPER FABRICATION REQUIRED TO BE RECTIFIED | Closed | 2026-07-04 | PS5-60-75 - Engine F Cooling system
PL-001653 | PS5-60-EA-2600A | C | M | 4.1:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-001655 | PS5-60-EA-2600A | C | M | 4.3:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-75 - Engine F Cooling system
PL-001656 | PS5-60-EA-2600A | A | M | 4.4:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-75 - Engine F Cooling system
PL-001657 | PS5-60-EA-2600A | A | M | 4.5:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-75 - Engine F Cooling system
PL-001658 | PS5-60-EA-2600B | C | M | 4:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-001659 | PS5-60-EA-2600B | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-75 - Engine F Cooling system
PL-001660 | PS5-60-EA-2600B | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-75 - Engine F Cooling system
PL-001661 | PS5-60-EA-2700A | C | M | 4:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-001662 | PS5-60-EA-2700A | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-76 - Engine G Cooling system
PL-001663 | PS5-60-EA-2700A | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-76 - Engine G Cooling system
PL-001664 | PS5-60-EA-2700B | C | M | 4:SOME FINS FOUND DAMAGE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-001665 | PS5-60-EA-2700B | C | M | 4.1:FOUND LOT OF PAPER AND LEAVES AND OTHER PARTICLES ON TOP OF COOLER BUNDLES | Originated |  | PS5-60-76 - Engine G Cooling system
PL-001666 | PS5-60-EA-2700B | A | M | 4.2:FOUND RUST ON FAN SUPPORTS DUE TO IMPROPER PAINTING | Closed | 2026-07-04 | PS5-60-76 - Engine G Cooling system
PL-001668 | PS5-74-UB-5100 | B | M | 4.1:All carbon steel (CS) bolts on the skid are rusted | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001669 | PS5-74-UB-5100 | B | M | 4.2:Equipment PS5-74-VF-1300B one name plate missing | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001670 | PS5-74-UB-5100 | C | M | 4.3:Color change observed on galvanizing of equipment and tubing supports. | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001671 | PS5-74-UB-5100 | C | M | 4.4:Skid base frame was found dirty and not properly cleaned prior to tansportation | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001672 | PS5-74-UB-5100 | B | M | 4.5:The outlet pressure gauge (PS5-74-PG-5103) needle is not functioning properly (Showing positive pressure ) | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001673 | PS5-74-UB-5100 | B | M | 4.6:Pressure gauge needle pointing below zero, may need to replace | Closed | 2026-07-04 | PS5-74-01 - N2 Generation Skid
PL-001674 | PS5-74-UB-5100 | C | M | 4.7:All stud bolts installed at the flange connections are over length | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001675 | PS5-74-UB-5100 | C | M | 4.8:Found rust of the SS earthing leg | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001676 | PS5-74-UB-5100 | C | M | 4.9:Welded area was not properly painted at all earthing boss. | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001677 | PS5-74-UB-5100 | C | M | 4.10:piping and branch connections were not properly painted | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001678 | PS5-74-UB-5100 | A | M | 4.11:Pipe to elbow weld joint found ruptured, Need to replace the elbow | Originated |  | PS5-74-01 - N2 Generation Skid
PL-001690 | PS5-61-IU-3100A | A | M | Oil leakage found from the transformer body nozzle weld area prior to installation | Closed | 2026-07-04 | PS5-25-02 - Crude Oil Export Pump A
PL-001691 | PS5-28-UO-8200 | C | M | 4:Minor damage found during inspection, suspected to be caused during transportation | Originated |  | PS5-28-11 - Open Drain Interceptor
PL-001692 | PS5-28-UO-8200 | C | M | 4.1:Detials are not clear in the PL/SRN | Originated |  | PS5-28-11 - Open Drain Interceptor
PL-001693 | PS5-28-UO-8200 | C | M | 4.2:Detials are not clear in the PL/SRN | Originated |  | PS5-28-11 - Open Drain Interceptor
PL-001694 | PS5-28-UO-8200 | B | M | 4.3:Minor damage observed inside the drainage interceptor. Also not in the correct position | Originated |  | PS5-28-11 - Open Drain Interceptor
PL-001695 | PS5-60-UZ-8900B | C | M | 4:It was observed that the insulation is not properly sealed | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-001696 | PS5-60-UZ-8900B | B | M | 4.1:Pressure gauge (PS5-60-PG-8905B)needle pointing below zero, may need to replace | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-001697 | PS5-60-UZ-8900B | B | M | 4.2:Pressure gauge (PS5-60-PG-8901B)needle pointing below zero, may need to replace | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-001698 | PS5-60-UZ-8900B | B | M | 4.3:Pressure gauge (PS5-60-PG-8903B)needle pointing positive, may need to replace | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-001699 | PS5-60-UZ-8900C | C | M | 4:It was observed that the insulation is not properly sealed | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-001700 | PS5-60-UZ-8900D | C | M | 4:It was observed that the insulation is not properly sealed | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-001701 | PS5-60-UZ-8900D | B | M | 4.1:Pressure gauge (PS5-60-PG-8906D)needle pointing below zero, may need to replace | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-001703 | PS5-60-UZ-8900E | C | M | 4.1:It was observed that the insulation is not properly sealed | Originated |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-001704 | PS5-60-UZ-8900F | C | M | 4:Diesel leak found, but source not yet identified (May be improper cleanning after FAT | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-001705 | PS5-60-UZ-8900F | C | M | 4.1:It was observed that the insulation is not properly sealed | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-001706 | PS5-60-UZ-8900F | B | M | 4.2:Pressure gauge (PS5-60-PG-8902F)needle pointing below zero, may need to replace | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-001708 | PS5-60-UZ-8900F | B | M | 4.4:Pressure gauge (PS5-60-PG-8905F)needle pointing below zero, may need to replace | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-001709 | PS5-60-UZ-8900G | C | M | 4:It was observed that the insulation is not properly sealed | Originated |  | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G
PL-001710 | PS5-60-UZ-8900G | B | M | 4.1:Pressure gauge (PS5-60-PG-8905G) needle pointing positive, may need to replace | Originated |  | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G
PL-001711 | PS5-60-UZ-8900G | B | M | 4.2:Pressure gauge (PS5-60-PG-8902G) needle pointing below zero, may need to replace | Originated |  | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G
PL-001712 | PS5-60-UZ-8900G | B | M | 4.3:Pressure gauge (PS5-60-PG-8903G)needle pointing below zero, may need to replace | Originated |  | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G
PL-001713 | PS5-61-IU-0001F | C | M | 4:Received Material with tag no. PS5-61-BE-0006A, As per PL PS5-61-IU-0001F. | Originated |  | PS5-60-16 - Power Generation Package F
PL-001714 | PS5-61-IU-0001F | C | M | 4.1:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | Originated |  | PS5-60-16 - Power Generation Package F
PL-001715 | PS5-61-IU-0001G | C | M | 4:Received Material with tag no. PS5-61-BE-0007A, As per PL PS5-61-IU-0001G. | Originated |  | PS5-60-19 - Power Generation Package G
PL-001716 | PS5-61-IU-0001G | C | M | 4.1:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | Originated |  | PS5-60-19 - Power Generation Package G
PL-001717 | PS5-61-IU-0001G | C | M | 4.2:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | Originated |  | PS5-60-19 - Power Generation Package G
PL-001722 | PS5-61-IU-0001G | C | M | 4.7:Transportation packing (Between radiators) were misplaced/ fallen down resulting damage on the edges of the radiators (May be severe) | Originated |  | PS5-60-19 - Power Generation Package G
PL-001724 | PS5-71-UZ-6400 | C | M | 4.1:Found insulation not properly sealed. | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-001725 | PS5-71-UZ-6400 | B | M | 4.2:Pressure gauge (PS5-71-PG-6401) needle pointing below zero, may need to replace | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-001726 | PS5-71-UZ-6400 | B | M | 4.3:Pressure gauge (PS5-71-PG-6417)needle pointing below zero, may need to replace | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-001727 | PS5-71-UZ-6400 | B | M | 4.4:Pressure gauge (PS5-71-PG-6416)needle pointing below zero, may need to replace | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-001728 | PS5-71-UZ-6400 | B | M | 4.5:Pressure gauge (PS5-71-PG-6414)needle pointing below zero, may need to replace | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-001729 | PS5-71-UZ-6400 | C | M | 4.6:One loose flame arrester delivered (Overage) without bolts, nuts, and gaskets | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-001730 | PS5-60-UR-8200A | B | M | 4:Pressure gauge (PS5-60-PI-8207A, PS5-60-PI-8205A, PS5-60-PI-8206A, PS5-60-PI-8208A)needle pointing positive reading, may need to replace | Originated |  | PS5-60-01 - Power Generation Package A
PL-001731 | PS5-60-UR-8200F | B | M | 4:Pressure gauge (PS5-60-TI-8308F, PS5-60-TI-8306F, PS5-60-PI-8208F, PS5-60-PI-8206F)needle pointing positive reading, may need to replace | Originated |  | PS5-60-16 - Power Generation Package F
PL-001732 | PS5-60-UR-8200E | B | M | 4:Pressure gauge (PS5-60-PI-8207E, PS5-60-PI-8208E, PS5-60-PI-8206E, PS5-60-PI-8205E) needle pointing positive reading, may need to replace | Originated |  | PS5-60-13 - Power Generation Package E
PL-001733 | PS5-60-UR-8200D | B | M | 4:Pressure gauge (PS5-60-PI-8207D, PS5-60-PI-8205D, PS5-60-PI-8208D, PS5-60-PI-8206D)needle pointing positive reading, may need to replace | Originated |  | PS5-60-10 - Power Generation Package D
PL-001734 | PS5-60-UR-8200C | B | M | 4:Pressure gauge (PS5-60-PI-8207C, PS5-60-TI-8306C, PS5-60-PI-8206C, PS5-60-PI-8208C)needle pointing positive reading, may need to replace | Originated |  | PS5-60-07 - Power Generation Package C
PL-001735 | PS5-60-UR-8200B | B | M | 4:Pressure gauge (PS5-60-PI-8207B,PS5-60-PI-8205B, PS5-60-PI-8206B, PS5-60-PI-8208B) needle pointing positive reading, may need to replace | Originated |  | PS5-60-04 - Power Generation Package B
PL-001736 | PS5-60-UR-8300C | A | E | 4:"Temperature gauge found broken (PS5-60-TI-8308C)" | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-001737 | PS5-60-UR-8300C | B | E | 4.1:Tube support found missing during inspection | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-001738 | PS5-60-UR-8300C | A | M | 4.2:Found plate removed due to not proper welding. | Closed | 2026-07-04 | PS5-60-37 - Injector Tip Cooling Module C
PL-001739 | PS5-60-UR-8300F | B | M | 4:Found top plate is damaged | Closed | 2026-07-09 | PS5-60-40 - Injector Tip Cooling Module F
PL-001740 | PS5-60-UR-8300D | A | M | 4:Found plate removed due to not proper welding. | Closed | 2026-07-04 | PS5-60-38 - Injector Tip Cooling Module D
PL-001741 | PS5-60-UR-8300D | A | M | 4.1:Cracks found on end plate welding. One of the end plate dittached and fallen down. | Closed | 2026-07-04 | PS5-60-38 - Injector Tip Cooling Module D
PL-001742 | PS5-60-UR-8300D | B | M | 4.2:Found damage on top plate damaged | Closed | 2026-07-09 | PS5-60-38 - Injector Tip Cooling Module D
PL-001743 | PS5-60-UR-8300D | C | M | 4.3:"Detials not available so not checked " | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-001744 | PS5-60-LA-0002A | B | M | 4:Found panel base damage VMS system cabinet 1 | Originated |  | PS5-60-01 - Power Generation Package A
PL-001746 | PS5-60-EA-2300A | A | M | 4.1:Found rust on fan supports due to improper painting | Closed | 2026-07-04 | PS5-60-72 - Engine C Cooling system
PL-001747 | PS5-60-EA-2300A | C | M | 4.2:"Rust found on outside angle of Luve remote radiator PS5-60-EA-2300A" | Originated |  | PS5-60-72 - Engine C Cooling system
PL-001748 | PS5-60-EA-2300B | A | M | 4:Found rust on fan supports due to improper painting | Closed | 2026-07-04 | PS5-60-72 - Engine C Cooling system
PL-001749 | PS5-60-EA-2300B | C | M | 4.1:"Rust found on outside angle of Luve remote radiator PS5-60-EA-2300B" | Originated |  | PS5-60-72 - Engine C Cooling system
PL-001750 | PS5-60-SEA-0001 | C | M | 4:Gas Detection Panel PS5-60-SEA-001 arrived as per the packing list, while PS-60-GB-0003 arrived without packing list/SRN and is missing the battery. | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-001751 | PS5-60-UR-8300G | A | M | 4:Tube got severe bend due to the damage of top plate touching (PS5-60-EA-21200G) | Closed | 2026-07-04 | PS5-60-41 - Injector Tip Cooling Module G
PL-001752 | PS5-60-UR-8300G | A | M | 4.1:Tube got severe bend due to the damage of top plate touching (PS 5-60-EA-21100G) | Closed | 2026-07-04 | PS5-60-41 - Injector Tip Cooling Module G
PL-001753 | PS5-60-UR-8300G | A | M | 4.2:Stitch / tack welding broken and end plate displaced from it's location PS5-60-EA-21200G | Closed | 2026-07-04 | PS5-60-41 - Injector Tip Cooling Module G
PL-001754 | PS5-60-UR-8300G | B | M | 4.3:As per packing list, quantity of seal O-rings is 900, but received only 895 | Originated |  | PS5-60-41 - Injector Tip Cooling Module G
PL-001755 | PS5-60-UR-8200G | A | M | 4:As per packing list, 7 Senior Flexonics but received only 5 nos. | Originated |  | PS5-60-19 - Power Generation Package G
PL-001756 | PS5-60-UR-8200G | C | M | 4.1:"No details mentioned in the packing list SO NOT CHECKED (CAT Special tools)""No details mentioned in the packing list SO NOT CHECKED (CAT Special tools)" | Originated |  | PS5-60-19 - Power Generation Package G
PL-001757 | PS5-60-UR-8200G | C | M | 4.2:Paint damage found on oil breather line pipe during inspection | Originated |  | PS5-60-19 - Power Generation Package G
PL-001758 | PS5-60-UR-8200G | C | M | 4.3:Proper details not available for the materials in Colli no:33 | Originated |  | PS5-60-19 - Power Generation Package G
PL-001759 | PS5-60-UR-8200G | B | M | 4.4:During inspection, a leakage of glycerin was found at the pressure gauge. | Originated |  | PS5-60-19 - Power Generation Package G
PL-001760 | PS5-61-IU-0001D | B | M | 4:Signs of leakage were observed in three different locations | Originated |  | PS5-60-10 - Power Generation Package D
PL-001877 | PS5-71-IE-0002 | A | E | SFU bar neutral to be tighten | Completed |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-001915 | PS5-61-IU-0001B | B | M | 4:Base plate of the transformer found damage on two foots after opening the wooden packing box. This might have happened due to the improper packing of the equipmentfromfactory | Originated |  | PS5-60-04 - Power Generation Package B
PL-001919 | PS5-83-EHO-0001A | B | M | 4:BOLTS AND NUTS FOR LIGHTING SUPPORT ARE MISING | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001920 | PS5-83-EHO-0001A | B | M | 4.1:BOLT FOR HAND RAIL BASE PLATE ARE MISSING | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001921 | PS5-83-EHO-0001A | B | M | 4.2: MINOR DAMAGE OBSERVED ON HVAC COMPRESSOR FINS | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001922 | PS5-83-EHO-0001A | A | M | 4.3:MAJOR DAMAGE (Might happened during transportation) ON THE MAINTENANCE DOOR AND THE CORNER STRUCTURE OF THE CONTAINER. Door could't open due to this. Need to replace these.Also lot of paint damages on the container. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001923 | PS5-83-EHO-0001A | B | M | 4.4: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001924 | PS5-83-EHO-0001A | C | M | 4.5:E-HOUSE CONTAINER OUT SIDE PAINT DAMAGE | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001925 | PS5-83-EHO-0001A | B | M | 4.6:LADDER CONNECTING PLATE BOLTS AND NUTS MISING | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001926 | PS5-83-EHO-0001A | B | M | 4.7:DOOR CAN NOT BE OPEN FROM OUTSIDE DUE TO THE IMPROPER FIXING OF THE HANDLE. NEED TO RECTIFY OR REPLACE BY VENDOR | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-001927 | PS5-83-EHO-0001B | B | M | 4:L CLAMP BOLT (HAND RAIL CONNECTION) MISSING | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001944 | PS5-83-EHO-0001B | B | M | 4.1: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001945 | PS5-83-EHO-0001B | A | M | 4.2:WALLMAX PIPE INLET MISSING | Closed | 2026-07-04 | PS5-25-03 - Crude Oil Export Pump B
PL-001946 | PS5-83-EHO-0001B | A | M | 4.3:WALLMAX PIPE CABLE ENTRY MISSING | Closed | 2026-07-04 | PS5-25-03 - Crude Oil Export Pump B
PL-001947 | PS5-83-EHO-0001B | C | M | 4.4:DOOR CAN NOT BE OPEN FROM OUTSIDE DUE TO THE IMPROPER FIXING OF THE HANDLE. NEED TO RECTIFY OR REPLACE BY VENDOR | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001948 | PS5-83-EHO-0001B | B | M | 4.5:E-HOUSE CONTAINER OUT SIDE PAINT DAMAGE | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-001949 | PS5-83-EHO-0001B | A | M | 4.6:LADDER CONNECTING PLATE BOLTS NUTS MISING | Completed |  | PS5-25-03 - Crude Oil Export Pump B
PL-001950 | PS5-83-EHO-0001C | A | M | 4:BOLT FOR HAND RAIL BASE PLATE ARE MISSING | Completed |  | PS5-25-04 - Crude Oil Export Pump C
PL-001951 | PS5-83-EHO-0001C | A | M | 4.1:TOE GUARD CONNECTING BOLTS ARE MISSING | Closed | 2026-07-04 | PS5-25-04 - Crude Oil Export Pump C
PL-001952 | PS5-83-EHO-0001C | A | M | 4.2:L CLAMP (HAND RAIL CONNECTION) MISSING | Closed | 2026-07-04 | PS5-25-04 - Crude Oil Export Pump C
PL-001953 | PS5-83-EHO-0001C | B | M | 4.3:L CLAMP BOLT (HAND RAIL CONNECTION) MISSING | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001954 | PS5-83-EHO-0001C | B | M | 4.4: BOLTS DAMAGED IN THE SIDE BOTTOM PORTION OF THE CONTAINER (Transportation damage) | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001956 | PS5-83-EHO-0001C | B | M | 4.6:E HOUSE CONTAINER DAMAGE AND PAINT DAMAGE | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001957 | PS5-83-EHO-0001C | B | M | 4.7:LADDER CONNECTING PLATE BOLTS NUTS MISING | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-001959 | PS5-71-PA-3300B | C | M | 4:The accumulator’s support was found on the floor during inspection. | Originated |  | PS5-71-05 - CFO Transfer Pump A/B
PL-001960 | PS5-71-PA-3300B | C | M | 4.1:The tube support was found on the floor during inspection. | Originated |  | PS5-71-05 - CFO Transfer Pump A/B
PL-001962 | PS5-71-PA-3400B | A | M | 4: Signs of leakage were observed in one location. | Originated |  | PS5-71-13 - CFO Service Pump A/B
PL-001963 | PS5-61-IU-0001D | B | E | Once opened the box, found the plastic cover containing bolts was not sealed. Only 3(out of 62) bolts were there inside the plastic cover-59nos (M10 X 38 stainless steel) bolts/nuts/ washersaremissing | Originated |  | PS5-60-10 - Power Generation Package D
PL-002335 | PS5-74-VA-1100 | C | M | 4:Found paint damaged at ladder,davit and platform angle | Originated |  | PS5-74-03 - Nitrogen Receiver
PL-002336 | PS5-61-IK-0001 | B | E | PS005-E&I-ALL-PL-2439 - ALL CABLE COMPARTMENTS: LABELS FROM OUTGOING FEEDERS SHALL BE BLACK/BROWN/GREY COLOURS | Closed | 2026-09-02 | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-002340 | PS5-61-IJ-0010 | B | E | PS005-E&I-ALL-PL-2451 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | Originated |  | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010)
PL-002341 | PS5-61-IJ-0011 | B | E | PS005-E&I-ALL-PL-2452 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-002344 | PS5-61-IK-0001 | B | E | PS005-E&I-ALL-PL-2440 - ALL DRAWERS: FINAL PROTECTION SETTINGS NOT SET COMPLETELY IN DRAWERS | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-002347 | PS5-61-IJ-0001 | B | E | PS005-E&I-ALL-PL-2448 - B04 Cell : Missing 1 set of Mechanical Key Lock = 2 CAMLOCK + 1 Key + 2 Spacer with serial number PH3212 (diameter rear side 10mm) was damage | Closed | 2026-08-05 | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-002349 | PS5-08-15CB-1001 | A | T | PS005-E&I-M4-PL-2586 - Flood light to be tested in tanzania and to be included in the ISMS SAT. | Originated |  | PS5-08-15 - Security Data Network (SII SP3 SEC)
PL-002350 | PS5-08-85DC-1007 | A | T | PS005-E&I-ETC-PL-2340 - Battery room door contact TBC if Atex required | Closed | 04-Aug-26 | PS5-08-85 - Access Control, POB & e-Mustering
PL-002361 | PS5-09-ACU-0007A-CD01 | A | E | PS005-E&I-M4-PL-2366 - Cable One Side Termination (COW) | Closed | 2026-07-24 | PS5-09-05 - HVAC for EITS Building
PL-002365 | PS5-06-GB-0001A-CS01 | A | E | PS005-E&I-ALL-PL-1584 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002366 | PS5-06-GB-0001A-CS03 | A | E | PS005-E&I-ALL-PL-1587 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002367 | PS5-06-GB-0001A-CS02 | A | E | PS005-E&I-ALL-PL-1590 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002368 | PS5-06-GB-0001A-CS04 | A | E | PS005-E&I-ALL-PL-1593 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002369 | PS5-06-GB-0001B-CS01 | A | E | PS005-E&I-ALL-PL-1895 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002370 | PS5-06-GB-0001B-CS03 | A | E | PS005-E&I-ALL-PL-1898 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002371 | PS5-06-GB-0001B-CS02 | A | E | PS005-E&I-ALL-PL-1901 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002372 | PS5-06-GB-0001B-CS04 | A | E | PS005-E&I-ALL-PL-1904 - Cable one side termination due to battery not install here (COW) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002373 | PS5-61-IE-0101-CA01 | A | T | PS005-E&I-M3-PL-2353 - Cable one side termination due to ECS Work station n/a (cow) | Originated |  | PS5-61-08 - Electrical Control System
PL-002374 | PS5-61-IE-0101-CA02 | A | T | PS005-E&I-M3-PL-2354 - Cable one side termination due to ECS Work station n/a (cow) | Originated |  | PS5-61-08 - Electrical Control System
PL-002375 | PS5-61-IE-0101-CA03 | A | T | PS005-E&I-M3-PL-2355 - Cable one side termination due to ECS Work station n/a (cow) | Originated |  | PS5-61-08 - Electrical Control System
PL-002378 | PS5-83-OB-0001 | A | B | PS005-E&I-M3-PL-2494 - Cable Still Coiled o top ECS Panel and 15CB Panel | Closed | 2026-08-01 | PS5-83-01 - EITS Building
PL-002388 | PS5-08-23LA-1001-CV01 | A | T | PS005-E&I-ALL-PL-2558 - Coaxial cable to be tested | Originated |  | PS5-08-23 - VHF Trunk Radio System
PL-002389 | PS5-61-IJ-0001 | A | E | PS005-E&I-ALL-PL-2449 - CT Box Not installed and not inspected. | Closed | 30-Jul-26 | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-002408 | PS5-06-IER-0001A | A | E | PS005-E&I-ALL-PL-2587 - Ex stoper plug to be installed for spare hole MCCB Box A | Closed | 27-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002410 | PS5-06-IER-0001B | A | E | PS005-E&I-ALL-PL-2588 - Ex stoper plug to be installed for spare hole MCCB Box B | Closed | 27-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-002413 | PS5-61-IK-0001 | B | E | PS005-E&I-ALL-PL-2441 - INCOMERS: INCOMER A, B AND C MCT CONFIGURATION DOES NOT FIT THE FIELD CABLE SCHEDULE PROVIDED BY EPS IN DESIGN DOSSIER | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-002414 | PS5-61-JY-0001 | C | E | PS005-E&I-ALL-PL-2454 - Maintenance trolley for BlokSet Air Circuit Breakers is missing | Closed | 2026-01-19 | PS5-78-01 - Lifting and handling equipment
PL-002422 | PS5-04-PSC-0001 | A | I | PS005-E&I-M4-PL-0357 - Missing component BP3-68FD-03, BP468FD-04 | Closed | 2026-08-31 | PS5-04-04 - 33kV PCS System
PL-002423 | PS5-09-IES-0001 | C | E | PS005-HVA-ETC-PL-2254 - No access to operate Emergency stop | Closed | 2026-04-23 | PS5-09-05 - HVAC for EITS Building
PL-002430 | PS5-09-ACU-0007A | A | H | PS005-E&I-M6-PL-2308 - One side cable coil /cow | Closed | 2026-03-25 | PS5-09-05 - HVAC for EITS Building
PL-002431 | PS5-09-ACU-0007B | A | H | PS005-E&I-M6-PL-2309 - One side cable coil /cow | Closed | 2026-03-25 | PS5-09-05 - HVAC for EITS Building
PL-002448 | PS5-01-LA-0001-CL01 | A | E | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | Originated |  | PS5-0H-01 - HIPPS
PL-002449 | PS5-01-LA-0001-CL02 | A | E | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | Originated |  | PS5-0H-01 - HIPPS
PL-002476 | PS5-61-IK-0001 | B | E | PS005-E&I-ALL-PL-2442 - Ring Ethernet cat6 Cables that are extended with coupler to be replaced by longer ones, and should pass through suitable cable opening. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-002477 | PS5-02-SGF-0010 | C | S | PS005-E&I-ALL-PL-2453 - Safety Kit that are supplied and installed in the substaion have some missing contents, to be check to match Doc. No. UT-MID-60-SSF1-120001 | Closed | 2025-12-05 | PS5-02-01 - Miscellaneous Safety equipment
PL-002484 | PS5-01-LA-0001-CC04 | A | I | PS005-E&I-M6-PL-1501 - Termination need to completed in drawing not mention for terminal block AN terminal number in panel ( PS5-01-LA-0001) | Completed |  | PS5-0H-01 - HIPPS
PL-002490 | PS5-61-IE-0002-CA07 | A | T | PS005-E&I-M2-PL-1347 - Update cable schedule and termination drawing to be confirm by enginnering | Closed | 2026-05-19 | PS5-61-08 - Electrical Control System
PL-002491 | PS5-61-IE-0002-CA08 | A | T | PS005-E&I-M2-PL-1349 - Update cable schedule and termination drawing to be confirm by enginnering | Closed | 2026-05-19 | PS5-61-08 - Electrical Control System
PL-002492 | PS5-61-IE-0002-CA09 | A | T | PS005-E&I-M2-PL-1351 - Update cable schedule and termination drawing to be confirm by enginnering | Closed | 2026-05-19 | PS5-61-08 - Electrical Control System
PL-002493 | PS5-61-IE-0002-CA10 | A | T | PS005-E&I-M2-PL-1353 - Update cable schedule and termination drawing to be confirm by enginnering | Closed | 2026-05-19 | PS5-61-08 - Electrical Control System
PL-002494 | PS5-61-IE-0002-CA11 | A | T | PS005-E&I-M2-PL-1355 - Update cable schedule and termination drawing to be confirm by enginnering | Closed | 2026-05-19 | PS5-61-08 - Electrical Control System
PL-002495 | PS5-61-IE-0002-CA12 | A | T | PS005-E&I-M2-PL-1357 - Update cable schedule and termination drawing to be confirm by enginnering | Closed | 2026-05-19 | PS5-61-08 - Electrical Control System
PL-002496 | PS5-08-13CB-1001 | A | T | PS005-E&I-M1-PL-2325 - Utilities power not tested, to be tested in tanzania | Originated |  | PS5-08-13 - Safety Data Network (SII SP3 SAF)
PL-002497 | PS5-08-11CB-1001 | A | T | PS005-E&I-M1-PL-2326 - Utilities power not tested, to be tested in tanzania | Originated |  | PS5-08-11 - Corporate LAN (SIE)
PL-002498 | PS5-08-35CB-1001 | A | T | PS005-E&I-M1-PL-2327 - Utilities power not tested, to be tested in tanzania | Originated |  | PS5-08-35 - Optical Transport Network
PL-002499 | PS5-08-15CB-1001 | A | T | PS005-E&I-M1-PL-2328 - Utilities power not tested, to be tested in tanzania | Originated |  | PS5-08-15 - Security Data Network (SII SP3 SEC)
PL-002505 | PS5-25-MOV-0012 | A | P | Valve damaged by the CPP contractor, It shall be repaired or replaced. | Originated |  | PS5-25-07 - Export Pipeline Pig Launcher
PL-002580 | PS5-74-VA-1100 | C | M | 4.1:Handrail bend due to mishandling | Originated |  | PS5-74-03 - Nitrogen Receiver
PL-002581 | PS5-74-VA-1100 | B | M | 4.2:As per packing list materials are ok. As per drawing we need more bolts. Which is not appearing in the packing list and didn't receive. (Bolt M16x45 w/nut & washer =20 nos and Bolt M12x45 w/nut & washer = 20 nos) | Closed | 2026-07-09 | PS5-74-03 - Nitrogen Receiver
PL-002589 | PS5-60-TR-4400 | B | M | 4.1:The vertical ladder top cage hoop farication is not correct. Required mirror emage of the present fabricated cage hoop | Closed | 2026-07-09 | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-002590 | PS5-01-TR-4300 | A | M | 4:During inspection, we found the 2" pipe weld at the bottom of the tank (Branch weld joint) is totally broken | Closed | 2026-07-04 | PS5-01-05 - Foam Skid
PL-002591 | PS5-01-TR-4300 | A | M | 4.1:The PS4-01-UV-8700 skid was received here instead of the PS5 skid to be replaced with correct one | Closed | 2025-11-27 | PS5-01-05 - Foam Skid
PL-002592 | PS5-01-TR-4300 | A | M | 4.2:Four flange connections with tag number PS4 have been identified and verified during inspection | Closed | 2025-11-27 | PS5-01-05 - Foam Skid
PL-002593 | PS5-28-PR-3900A | C | M | 4:During the inspection, it was found that the flange face area had been painted | Originated |  | PS5-28-17 - Reinjection Pump
PL-002594 | PS5-28-PR-3900A | A | M | 4.1:During the inspection, a significant oil leakage was detected on the pump body(Joint) | Originated |  | PS5-28-17 - Reinjection Pump
PL-002595 | PS5-28-PR-3900A | C | M | 4.2:It was observed that the stud installed was shorter than the required length. | Originated |  | PS5-28-17 - Reinjection Pump
PL-002596 | PS5-28-PR-3900A | A | M | 4.3:During the inspection, a significant oil leakage was detected on the boll vave(Joint) | Completed |  | PS5-28-17 - Reinjection Pump
PL-002597 | PS5-28-PR-3900A | C | M | 4.4:Found paint damage at pump area | Originated |  | PS5-28-17 - Reinjection Pump
PL-002598 | PS5-28-PR-3900B | A | M | 4:During inspection, a noticeable oil leakage was detected at the discharge valve area of PS5-28-APO-3901B | Completed |  | PS5-28-17 - Reinjection Pump
PL-002599 | PS5-28-PR-3900B | C | M | 4.1It was observed that the stud installed was shorter than the required length. | Originated |  | PS5-28-17 - Reinjection Pump
PL-002600 | PS5-01-UV-8700 | C | M | 4:Paint damage and U clamp support missing | Originated |  | PS5-01-05 - Foam Skid
PL-002601 | PS5-01-UV-8700 | C | M | 4.1:Found paint damage | Originated |  | PS5-01-05 - Foam Skid
PL-002602 | PS5-01-UV-8700 | A | M | 4.2:Hilti hit-HY-200-A was expired | Closed | 2026-07-04 | PS5-01-05 - Foam Skid
PL-002603 | PS5-01-UV-8700 | B | M | 4.3:PS5-01-IE-0001A support clamp bolt missing and support clamp was broken-01-IE-0001A support clamp bolt missing and support clamp was broken | Originated |  | PS5-01-05 - Foam Skid
PL-002604 | PS5-01-UV-8700 | B | M | 4.4:Junction box stand 2 bolts are missing | Originated |  | PS5-01-05 - Foam Skid
PL-002605 | PS5-01-UV-8700 | A | M | 4.5:1" recirculating line piping flange connection bolts 8 nos and spool 2" flange connection bolts 8 nos are not available with spool or skid | Originated |  | PS5-01-05 - Foam Skid
PL-002607 | PS5-71-VSV-1200 | B | M | 4.1:During the inspection, it was found that the flange face area had Found bend on the nozzle(N5) - Might have happened due to external impact. Also observed paint damage in the location.(No paint damage on the flange or damageonthebolts)been painted | Closed | 2026-09-04 | PS5-71-20 - Diesel Fuel Day Tank
PL-002608 | PS5-01-PA-3200A | B | M | 4:During the inspection, it was found that the gasket (331ID × 348OD × 1.5T) was damaged | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002609 | PS5-01-PA-3200A | B | M | 4.1:As per the packing list (Equipment No. 12286.347), 12 pieces of 1/2" BSP female elbows were listed; they were not received. | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002610 | PS5-01-PA-3200A | B | M | 4.2:As per the packing list, 4 units of Stud Coupling A-Lok 8MSC8N-316 were scheduled for delivery; only 2 units were received.. | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002611 | PS5-01-PA-3200A | A | M | 4.3:Hole diameter for the anchor bolts are is lesser than anchor bolt diameter. Need to enlarge the hole diameter to fit withanchorbolt | Completed |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002612 | PS5-01-PA-3200A | C | M | 4.4:Oil observed at the pump base frame floor area (Oil indicator glass not fixed properly). | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002613 | PS5-01-PA-3200A | B | M | 4.5:As per the packing list (Equipment No. 13472-711-076-7), 1/2" OD × 16SWG W/T Tubes (4000 mm ) but not received. | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002614 | PS5-01-PA-3200B | B | M | 4:During the inspection, it was found that the gasket (331ID × 348OD × 1.5T) was damaged | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002615 | PS5-01-PA-3200B | B | M | 4.1:As per the packing list (Equipment No. 12286.347), 12 pieces of 1/2" BSP female elbows were listed; they were not received. | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002616 | PS5-01-PA-3200B | B | M | 4.2:As per the packing list, 4 units of Stud Coupling A-Lok 8MSC8N-316 were scheduled for delivery; only 2 units were received.. | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002617 | PS5-01-PA-3200B | A | M | 4.3:Hole diameter for the anchor bolts are is lesser than anchor bolt diameter. Need to enlarge the hole diameter to fit withanchorbolt | Completed |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002618 | PS5-01-PA-3200B | C | M | 4.4:Oil observed at the pump base frame floor area (Oil indicator glass not fixed properly). | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002619 | PS5-01-PA-3200B | B | M | 4.5:As per the packing list (Equipment No. 13472-711-076-7), 1/2" OD × 16SWG W/T Tubes (4000 mm ) but not received. | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-002621 | PS5-01-PA-3100B | B | M | 4.1:Plug missing on the 2 nos valves (with pressure gauge) firewaterpumpB | Originated |  | PS5-01-03 - Fire Water Pump B
PL-002622 | PS5-01-PA-3100B | B | M | 4.2:Oil was found in this area (may be oil leakage) | Originated |  | PS5-01-03 - Fire Water Pump B
PL-002623 | PS5-01-PA-3100B | B | M | 4.3:The cover plate and nuts and bolts are missing. | Originated |  | PS5-01-03 - Fire Water Pump B
PL-002624 | PS5-01-PA-3100B | C | M | 4.4:Observed paint damage on the hose | Originated |  | PS5-01-03 - Fire Water Pump B
PL-002625 | PS5-01-PA-3100B | A | M | 4.5:Damage observed on pressure gauge | Originated |  | PS5-01-03 - Fire Water Pump B
PL-002626 | PS5-01-PA-3100B | B | M | 4.6:Rubber bush / shock absorber found damage. | Originated |  | PS5-01-03 - Fire Water Pump B
PL-002627 | PS5-01-UZ-6900 | B | M | 4:During the inspection, some nuts of the overhead pipe supports were found on the floor to be reinstated | Originated |  | PS5-01-10 - Water Mist Package
PL-002634 | PS5-83-OB-0001 | A | M | 4.1:As per the packing list 2 units of EDS-C1-106-002 were scheduled for delivery; only 1 unit was received. | Originated |  | PS5-83-01 - EITS Building
PL-002635 | PS5-83-OB-0001 | B | M | 4.2:"As per the packing list PS5-3BC-FP-01 Coverplate on deckplate 1Qty listed; that was not received" | Originated |  | PS5-83-01 - EITS Building
PL-002636 | PS5-83-OB-0001 | B | M | 4.3:As per the packing list -PS5-A34-03 Dripping Nose 1Qty listed;that was not received | Completed |  | PS5-83-01 - EITS Building
PL-002637 | PS5-83-OB-0001 | B | M | 4.4:As per the packing list 6 units of EDS-C1-106-002 were scheduled for delivery; only 2 unit were received. | Originated |  | PS5-83-01 - EITS Building
PL-002638 | PS5-83-OB-0001 | A | M | 4.5:As per the packing list -BOLT M10*40HDG 40Qty listed;they were not received | Originated |  | PS5-83-01 - EITS Building
PL-002639 | PS5-83-OB-0001 | A | M | 4.6:As per the packing list -CLAMP LADDER 40 Qty listed;they were not received | Closed | 2026-07-09 | PS5-83-01 - EITS Building
PL-002640 | PS5-83-OB-0001 | B | M | 4.7:As per the packing list 57 units of shroud were scheduled for delivery; only 50 unit were received. | Originated |  | PS5-83-01 - EITS Building
PL-002641 | PS5-83-OB-0001 | B | M | 4.8:As per the packing list 414 units of shroud were scheduled for delivery; only 337 unit were received. | Originated |  | PS5-83-01 - EITS Building
PL-002642 | PS5-83-OB-0001 | B | M | 4.9:Flashing column (inside the module )PS5-FLS-RF10 is shorter in lenghth and it can not be fix | Closed | 2026-07-09 | PS5-83-01 - EITS Building
PL-002643 | PS5-83-OB-0001 | B | M | 4.10: item cut on one side due to deep scratch | Originated |  | PS5-83-01 - EITS Building
PL-002644 | PS5-83-OB-0001 | A | E | 4.11:NOT COMPLETE ONE PART IS MISSING | Originated |  | PS5-83-01 - EITS Building
PL-002645 | PS5-83-OB-0001 | B | M | 4.12:External holes (for the alignment of bolt ) are missalinged /need to modify the hole, Rust found near the joint between module 2&3 | Closed | 2026-07-09 | PS5-83-01 - EITS Building
PL-002646 | PS5-83-OB-0001 | B | M | 4.13:Holes not provided/drilled/tap for installing deck cover plate Between Module 5/6, 6/3, 5/2, 3/2 | Originated |  | PS5-83-01 - EITS Building
PL-002647 | PS5-83-OB-0001 | B | M | 4.14:Duct support ,light support,cable tray misplaced/ collapsed from the location | Originated |  | PS5-83-01 - EITS Building
PL-002648 | PS5-83-OB-0001 | B | M | 4.15:Flashing column (inside the module 5/6) PS5-FLS-RF10 is shorter in lenghth and it can not be fix. | Closed | 2026-07-09 | PS5-83-01 - EITS Building
PL-002649 | PS5-83-OB-0001 | B | M | 4.16:EITS - IT room door not fixed properly and water coming inside during the rain (manufacturing issue) | Originated |  | PS5-83-01 - EITS Building
PL-002653 | PS5-61-ISO-9005-05-CS01 | A | E | PS005-E&I-ALL-PL-1625 - Cable one side termination due to panel not install yet COW - TAG change to be done | Completed |  | PS5-61-08 - Electrical Control System
PL-002655 | PS5-09-IES-0002 | C | E | PS005-HVA-ETC-PL-2254 - No access to operate Emergency stop | Closed | 2025-11-27 | PS5-09-05 - HVAC for EITS Building
PL-002656 | PS5-01-LA-0001-CL03 | A | I | PS005-E&I-ALL-PL-2589 - Power cable HIPPS Cabinet in General Batch 2 Should be replaced by Fire resistance (Orange cable) | Originated |  | PS5-0H-01 - HIPPS
PL-002662 | PS5-01-UB-6100 | C | I | PS005-E&I-ALL-PL-2426 - Special tool to reset Fire suppression solenoid valve to be provided. One by substation | Closed | 2025-12-22 | PS5-01-09 - Inergen for EITS Building
PL-002663 | PS5-61-ISR-0101 | B | E | 4:IP washers are damaged | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-002664 | PS5-61-ISR-0101 | B | E | 4.1:Some cable entries are installed without IPwashers | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-002665 | PS5-61-ISR-0102 | A | M | 4:Pressure gauge glass was dislodged, and the gauge found in a bent position | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-002666 | PS5-61-ISR-0102 | C | M | 4.1:Oil barrel leakage (Since bottom side of the barrel was leaking turnedupsidedown) | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-002667 | PS5-09-PA-84500A | C | M | 4:There is no mention of the tag number on the name plate. | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-002668 | PS5-09-PA-84500B | C | M | 4:There is no mention of the tag number on the name plate. | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-002669 | PS5-09-PA-84500B | A | M | 4.1:Rust was found on the coupling / coupling hub during the inspection. | Closed | 2026-07-09 | PS5-09-03 - HVAC for Generator Building
PL-002670 | PS5-60-TR-4300 | C | M | 4:As per the packing list, 2 numbers of compressed non-asbestos fibre gaskets; Received 4 numbers were received, resulting in an overage of 2 numbers. | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-002672 | PS5-01-PA-3100B | A | M | Pressure gauges removed from the equipment by CPP preservation/ material team to be reistated after piping installation | Originated |  | PS5-01-03 - Fire Water Pump B
PL-002868 | PS5-61-IE-0002 | B | E | ECS-iVT - 2024-05-29-007 SFP (100Mb or 1Gb) to provide for Ethernet switches, SW02A/SW02B | Originated |  | PS5-61-08 - Electrical Control System
PL-002874 | PS5-25-SDV-0054B | B | I | 4:The panel board was found to have fallen from its bolt support during transportation. The bolt locations were cracked and torn due to excessive load. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-002875 | PS5-25-SDV-0054C | B | I | 4:The panel board was found to have fallen from its bolt support during transportation. The bolt locations were cracked and torn due to excessive load. | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-003051 | PS5-61-JY-0001 | C | M | PS005-E&I-COW-1004 - Maintenance trolley for BlokSet : oil filling required | Closed | 2026-08-08 | PS5-78-01 - Lifting and handling equipment
PL-003059 | PS5-61-IK-0001 | B | E | PS005-E&I-COW-1014 - ATS PLC SOFTWARE (I/O MAPPING) TO BE UPDATED AND TESTED | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-003063 | PS5-06-IG-0002 | C | E | PS005-E&I-COW-1018 - Missing Terminal ID X05 and Terminal numbers 1 to 8 | Closed | 27-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-003068 | PS5-06-IG-0002 | B | E | PS005-E&I-COW-1023 - STS SETTINGS TO BE SET | Originated |  | PS5-06-01 - AC UPS - EITS Building
PL-003077 | PS5-61-IG-0015 | A | E | Vendor TB minimum termination capacity is 25 sqmm. Vendor to provide terminals suitable 16 sqmm and to be installed by Construction CTR. | Originated |  | PS5-62-10 - CRO Generator Building Normal L&SP DB - PS5-61-IG-0015
PL-003078 | PS5-05-IG-0026 | A | E | Vendor TB minimum termination capacity is 25 sqmm. Vendor to provide terminals suitable 6 sqmm and to be installed by Construction CTR. | Originated |  | PS5-62-07 - CRO Generator Electrical Building Emergency Lighting DB - PS5-05-IG-0026
PL-003254 | PS5-25-PIT-0001 | A | I | Range calibration to be done | Originated |  | PS5-25-01 - Export Pipeline Pig Receiver
PL-003259 | PS5-28-PIT-0041 | A | I | Range calibration to be done | Originated |  | PS5-28-17 - Reinjection Pump
PL-003294 | PS5-03-SFSC-0001 | A | I | Cyber-FAT-120 Moxa switch for SIS PS2-03-SW-0001 was tested in Vitrolles, the remaining moxa sw are in Batam or they have been already sent to site. | Originated |  | PS5-04-05 - 33kV SIS/FGS System
PL-003415 | PS5-01-PAL-6101 | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | Closed | 24-Jul-26 | PS5-01-09 - Inergen for EITS Building
PL-003416 | PS5-01-PAL-6102 | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | Closed | 24-Jul-26 | PS5-01-09 - Inergen for EITS Building
PL-003417 | PS5-01-PAL-6103 | A | I | PS005-E&I-ALL-PL-2608 - PAL Cable that currently installed Flame Retardant (E253359) shall be replace with Fire Resistan cable IEC60331 (Orange). | Closed | 24-Jul-26 | PS5-01-09 - Inergen for EITS Building
PL-003473 | PS5-61-IV-0001A-CH01 | A | E | 7: | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-003579 | PS5-60-UR-8100A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHALL BE COMPLETED (DISCIPILINE - PIPING) | Closed | 2026-09-04 | PS5-60-01 - Power Generation Package A
PL-003580 | PS5-60-UR-8100A | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | Originated |  | PS5-60-01 - Power Generation Package A
PL-003581 | PS5-60-UR-8100B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | Closed | 2026-09-04 | PS5-60-04 - Power Generation Package B
PL-003582 | PS5-60-UR-8100B | B | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | Originated |  | PS5-60-04 - Power Generation Package B
PL-003583 | PS5-60-UR-8100C | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | Closed | 2026-09-04 | PS5-60-07 - Power Generation Package C
PL-003584 | PS5-60-UR-8100C | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | Originated |  | PS5-60-07 - Power Generation Package C
PL-003585 | PS5-60-UR-8100D | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | Closed | 2026-09-05 | PS5-60-10 - Power Generation Package D
PL-003586 | PS5-60-UR-8100D | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | Originated |  | PS5-60-10 - Power Generation Package D
PL-003587 | PS5-60-UR-8100E | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | Closed | 2026-09-05 | PS5-60-13 - Power Generation Package E
PL-003588 | PS5-60-UR-8100E | B | M | 10.1:FINAL ALIGNMENT SHULD BE DONE | Originated |  | PS5-60-13 - Power Generation Package E
PL-003589 | PS5-60-UR-8100F | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | Closed | 2026-09-05 | PS5-60-16 - Power Generation Package F
PL-003590 | PS5-60-UR-8100F | B | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | Originated |  | PS5-60-16 - Power Generation Package F
PL-003591 | PS5-60-UR-8100G | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT SHAL BE COMPLETED (DESCIPILINE - PIPING) | Closed | 2026-09-05 | PS5-60-19 - Power Generation Package G
PL-003592 | PS5-60-UR-8100G | B | M | 10.1:FINAL ALIGNMENT SHOULD BE DONE | Originated |  | PS5-60-19 - Power Generation Package G
PL-003593 | PS5-83-OB-0001_Installation | A | M | Structural bolts shall be properly secured & tightened all over the EITS Building area | Closed | 2026-02-24 | PS5-83-01 - EITS Building
PL-003594 | PS5-83-OB-0001_Installation | B | B | Proper Leveling, compaction, gravel fill required for the whole EITS building area. | Originated |  | PS5-83-01 - EITS Building
PL-003595 | PS5-83-OB-0001_Installation | A | M | Grating Clips shall be properly fastened and tightened | Closed | 2026-02-24 | PS5-83-01 - EITS Building
PL-003596 | PS5-83-OB-0001_Installation | B | M | External covers outside the EITS building found gaps, screw damages & holes mismatch. | Originated |  | PS5-83-01 - EITS Building
PL-003597 | PS5-83-OB-0001_Installation | B | B | Proper finishing required for the EITS building foundations. | Originated |  | PS5-83-01 - EITS Building
PL-003600 | PS5-83-OB-0001_Installation | B | E | Sprinkler to be installed after GALT. | Originated |  | PS5-83-01 - EITS Building
PL-003601 | PS5-09-ACU-0007_OUTDOOR_INSTALLATION | A | M | Anchor bolts need to be tightened for HVAC ACU units. | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-003602 | PS5-83-OB-0001_Installation | B | M | Handrail Splice needs to be Welded and Painted at East side area | Closed | 2026-02-24 | PS5-83-01 - EITS Building
PL-003605 | PS5-83-OB-0001_Installation | A | H | All HVAC ducts were misaligned with the ACU units. | Originated |  | PS5-83-01 - EITS Building
PL-003606 | PS5-83-OB-0001_Installation | A | E | Earthing bonders need to be installed all over structural connection. | Originated |  | PS5-83-01 - EITS Building
PL-003608 | PS5-83-OB-0001_Installation | A | E | For all Inergen lines U-bolts tightening & Torquing shall be done before GALT | Originated |  | PS5-83-01 - EITS Building
PL-003609 | PS5-83-OB-0001_Installation | A | M | Shutoff Dampers were not installed above the HVAC ACU units (4 Dampers) | Closed | 2026-02-24 | PS5-83-01 - EITS Building
PL-003610 | PS5-83-OB-0001_Installation | A | H | HVAC Ducts leak test shall be performed after finishing the whole installations | Originated |  | PS5-83-01 - EITS Building
PL-003611 | PS5-83-OB-0001_Installation | A | B | Missing two elbows (3019F and 3019G) | Originated |  | PS5-83-01 - EITS Building
PL-003612 | PS5-83-OB-0001_Installation | A | P | MCT not provided for the Inergen pipes which are entering into the Inergen Package | Closed | 2026-05-12 | PS5-83-01 - EITS Building
PL-003615 | PS5-83-OB-0001_Installation | B | E | All EIT cable tray, Ladder, tray supports shall be installed | Originated |  | PS5-83-01 - EITS Building
PL-003616 | PS5-83-OB-0001_Installation | A | E | Electrical earthing around the building shall be completed. | Closed | 2026-02-24 | PS5-83-01 - EITS Building
PL-003617 | PS5-61-IU-0011 | A | E | 4:During inspection, the junction box fell down due to improper fixing. The item was dispatched without being securely installed. | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-003618 | PS5-61-IU-0011 | B | E | 4.1:No cable glands are installed in the DECT MDU PANEL | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-003619 | PS5-61-IU-0011 | B | E | 4.2:All installed cables are directly fixed to the transformer without cable trays and/or rigid conduit pipes. | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-003620 | PS5-61-IU-0011 | B | E | 4.3:"At the commissioning stage, it is necessary to verify the functionality of the equipment and confirm the absence of any hidden defects. Because panel was unfixed." | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-003621 | BF_PS5-61-IU-0010 | B | E | 4:No cable glands are installed in the DECT MDU PANEL | Originated |  | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010)
PL-003622 | PS5-61-IU-0010 | B | E | 4.1:All installed cables are directly fixed to the transformer without cable trays and/or rigid conduit pipes. | Originated |  | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010)
PL-003623 | PS5-01-PA-3100A | B | M | 4:All the jack bolts are missing on the base frame of the pump | Originated |  | PS5-01-02 - Fire Water Pump A
PL-003624 | PS5-01-PA-3100A | A | M | 4.1:22 batteries had a voltage below 1V, 6 batteries had a voltage below 1.2V | Originated |  | PS5-01-02 - Fire Water Pump A
PL-003625 | PS5-01-PA-3100A | A | M | 4.2:Silencer not received along with the pump | Completed |  | PS5-01-02 - Fire Water Pump A
PL-003648 | PS5-01-UZ-610 | A | M | 4:As per the packing list, a 0.18-liter Nitrogen (N₂) cylinder is specified with a filling pressure of 200 bar. However, upon receipt at PS5-01-UZ-610, two cylinders were found with pressures of 1300 psi (89.6 Bar), which are below the specified 200 bar requirement. | Originated |  | PS5-01-11 - Inergen for Power Gen Building
PL-003649 | PS5-71-UN-7200 | B | M | 4:"Spare parts have arrived; but no details are mentioned in the packing list. ( gaskets-2 pcs 3/4"" 150# 4 pcs 1"" 150# 4 pcs 1 1/2"" 150# 5 pcs 2"" 150"" 3 pcs 4"" 150# 2 set lamps fuses and connectors (SIBA FUSE 5X20 T 125MA DS10) 1 PCS DIGITAL BARRIER dek-oe-24dc/100k. 1 pcs repeater power supply (Analog barrier) MACX MCR-SL-RPSSI-2I. )" | Originated |  | PS5-71-02 - CFO Allocation Metering Package
PL-003654 | PS5-28-PA-3700A | B | M | Coupling hub inside dia is not matching with the shaft dia of pump and motor | Closed | 2026-07-09 | PS5-28-04 - Closed Drain Drum and Pump 02
PL-003655 | PS5-28-PA-3700B | A | M | Coupling hub inside dia is not matching with the shaft dia of pump and motor | Closed | 2026-07-04 | PS5-28-04 - Closed Drain Drum and Pump 02
PL-003692 | PS5-75-UI-6100 | B | I | Level Gauge FAT not conducted as the Specific gravity of the water does not allow the instrument float to float. | Originated |  | PS5-75-02 - Biocide Injection Package
PL-003701 | PS5-61-IE-0001 | B | E | ECS-iFAT-2024-07-02-011 Keyboard and mouse lose connection after power recycle from MCB on ECS Server A & B | Originated |  | PS5-61-08 - Electrical Control System
PL-003706 | PS5-61-IE-0001 | B | E | ECS-ECS - 20255-08-12-003 Configure the static route for ALL ECS/PCS connection | Originated |  | PS5-61-08 - Electrical Control System
PL-003714 | PS5-71-TR-4100 | A | M | 4:As per the drawing, the deluge piping should be galvanized Carbon steel, but it was received without a galvanized coating. | Closed | 2026-07-04 | PS5-71-04 - CFO Storage Tank
PL-003715 | PS5-71-TR-4100 | A | M | 4.1:SL NO-11, M10 'U' BOLT - 2" PIPE + 4NUTS (STD) NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003716 | PS5-71-TR-4100 | A | M | 4.2:SL NO - 14 , GASKET 3MM NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003717 | PS5-71-TR-4100 | A | M | 4.3: SL NO - 17, WASHER NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003718 | PS5-71-TR-4100 | A | M | 4.4:SL NO - 20 , GASKET 762O.D.x600I.D.x1.5THK NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003719 | PS5-71-TR-4100 | A | M | 4.5:SL NO - 24 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003720 | PS5-71-TR-4100 | A | M | 4.6:SL NO - 26 , GASKET 1.5 THK., 6"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003721 | PS5-71-TR-4100 | A | M | 4.7:SL NO - 29 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003722 | PS5-71-TR-4100 | A | M | 4.8:SL NO - 32 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003723 | PS5-71-TR-4100 | A | M | 4.9:SL NO - 37 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003724 | PS5-71-TR-4100 | A | M | 4.10:SL NO - 38 , STUD+2NUTS-5/8" UNC NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003725 | PS5-71-TR-4100 | A | M | 4.11:SL NO - 54 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003726 | PS5-71-TR-4100 | A | M | 4.12:SL NO - 58 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | Closed | 14-May-26 | PS5-71-04 - CFO Storage Tank
PL-003727 | PS5-71-TR-4200 | A | M | 4:As per the drawing, the deluge piping should be galvanized carbon steel, but it was received without a galvanized coating. | Closed | 2026-07-04 | PS5-71-12 - CFO Service Tank
PL-003728 | PS5-71-TR-4200 | A | M | 4.1:SL NO - 61 , GASKET 762 ,O.D.x600,I.D.x1.5THK NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003729 | PS5-71-TR-4200 | A | M | 4.2:SL NO - 67 , GASKET 3MM NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003731 | PS5-71-TR-4200 | A | M | 4.4:SL NO - 70 , WASHER NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003732 | PS5-71-TR-4200 | A | M | 4.5:SL SL NO - 71 , HEX. NUTS M20 NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003733 | PS5-71-TR-4200 | A | M | 4.6:SL NO - 75 , WASHER O.D. 40 x I.D. 18 NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003734 | PS5-71-TR-4200 | A | M | 4.7:SL NO - 76 , SPLIT PIN-5Ø NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003735 | PS5-71-TR-4200 | A | M | 4.8:SL NO -77 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003736 | PS5-71-TR-4200 | A | M | 4.9:SL NO - 79 , GASKET 1.5 THK., 3"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003737 | PS5-71-TR-4200 | A | M | 4.10:SL NO - 82 , GASKET 4.5 THK., 10"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003738 | PS5-71-TR-4200 | A | M | 4.11:SL NO - 85 , GASKET 4.5 THK., 8"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003739 | PS5-71-TR-4200 | A | M | 4.12:SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003740 | PS5-71-TR-4200 | A | M | 4.13:SL NO - 90 , GASKET 4.5 THK., 3"-150# RF NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003741 | PS5-71-TR-4200 | A | M | 4.14:SL NO - 106 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003742 | PS5-71-TR-4200 | A | M | 4.15:SL NO - 111 , HEX.BOLT+NUTS+WASHER. M12X45 NOT RECEIVED | Closed | 14-May-26 | PS5-71-12 - CFO Service Tank
PL-003743 | PS5-71-TR-4400 | B | M | As per the packing list, 3 Nos. of 1/4" nipple are mentioned, but they have not been received. | Originated |  | PS5-71-15 - Diesel Fuel Storage Tank
PL-003744 | PS5-53-TR-4100 | B | M | As per the packing list, 3 Nos. of vortex breakers are mentioned, but they have not been received. | Completed |  | PS5-53-01 - Utility Water / Storage Tank
PL-004311 | PS5-60-VS-9100A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-004312 | PS5-60-VS-9100B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-004313 | PS5-60-VS-9100C | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-004314 | PS5-60-VS-9100D | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-004315 | PS5-60-VS-9100F | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | Closed | 2026-09-05 | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F
PL-004316 | PS5-60-VA-5100C | A | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-04 | PS5-60-30 - Air Receiver C & Air Regulator C
PL-004333 | PS5-60-YF-1700A | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-004334 | PS5-60-YF-1700A | C | E | 16.1:EARTHING TO BE DONE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-004335 | PS5-60-YF-1700B | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-004336 | PS5-60-YF-1700B | C | E | 16.1:EARTHING TO BE DONE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-004340 | PS5-78-JC-9100A | C | M | 25:ouch up paint will be carried out | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004341 | PS5-78-JC-9100B | C | M | 25:Touch-up painting will be carried out | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004342 | PS5-78-JC-9100C | C | M | 25:Touch-up painting will be carried out | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004343 | PS5-78-JC-9100D | C | M | 25:Touch-up painting will be carried out | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004344 | PS5-05-UR-8100 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-05-01 - Emergency Diesel Generator Package
PL-004345 | PS5-05-UR-8100 | A | M | 10.1: Flame arrester to be installed | Closed | 2026-07-04 | PS5-05-01 - Emergency Diesel Generator Package
PL-004346 | PS5-05-UR-8100 | B | M | 10.2:Final alignment to be verified | Originated |  | PS5-05-01 - Emergency Diesel Generator Package
PL-004347 | PS5-60-VA-5100A | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-28 - Air Receiver A & Air Regulator A
PL-004348 | PS5-60-VA-5100A | B | E | 23.1:EARTHING TO BE DONE | Originated |  | PS5-60-28 - Air Receiver A & Air Regulator A
PL-004349 | PS5-60-VA-5100B | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | Closed | 2026-09-05 | PS5-60-29 - Air Receiver B & Air Regulator B
PL-004350 | PS5-60-VA-5100B | B | E | 23.1:EARTHING TO BE DONE | Originated |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-004351 | PS5-60-VS-9100E | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(discipline-piping) | Closed | 2026-09-05 | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E
PL-004352 | PS5-60-VS-9100G | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G
PL-004353 | PS5-60-UZ-8900A | A | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-004354 | PS5-60-VA-5100D | A | E | 23:EARTHING TO BE DONE | Completed |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-004355 | PS5-60-VA-5100D | B | P | 23.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-31 - Air Receiver D & Air Regulator D
PL-004356 | PS5-60-VA-5100E | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-32 - Air Receiver E & Air Regulator E
PL-004357 | PS5-60-VA-5100E | B | E | 23.1:EARTHING TO BE DONE | Originated |  | PS5-60-32 - Air Receiver E & Air Regulator E
PL-004358 | PS5-60-VA-5100F | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-33 - Air Receiver F & Air Regulator F
PL-004359 | PS5-60-VA-5100F | B | E | 23.1: EARTHING TO BE DONE | Originated |  | PS5-60-33 - Air Receiver F & Air Regulator F
PL-004360 | PS5-60-VA-5100G | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-34 - Air Receiver G & Air Regulator G
PL-004361 | PS5-60-VA-5100G | B | E | 23.1: EARTHING TO BE DONE | Originated |  | PS5-60-34 - Air Receiver G & Air Regulator G
PL-004362 | PS5-60-YF-1700G | B | M | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G
PL-004363 | PS5-60-YF-1700G | B | E | 16.1: EARTHING TO BE DONE | Originated |  | PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G
PL-004364 | PS5-60-YF-1700F | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-004365 | PS5-60-YF-1700F | B | E | 16.1:EARTHING TO BE DONE | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-004366 | PS5-60-YF-1700E | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-004367 | PS5-60-YF-1700E | B | E | 16.1:EARTHING TO BE DONE | Originated |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-004368 | PS5-60-YF-1700D | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-004369 | PS5-60-YF-1700D | B | E | 16.1:EATRHING TO BE DONE | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-004370 | PS5-60-YF-1700C | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-004371 | PS5-60-YF-1700C | B | E | 16.1:EARTHING TO BE DONE | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-004372 | PS5-60-UR-8200A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-01 - Power Generation Package A
PL-004373 | PS5-60-UR-8200B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-04 - Power Generation Package B
PL-004374 | PS5-60-UR-8200C | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Closed | 2026-09-05 | PS5-60-07 - Power Generation Package C
PL-004375 | PS5-60-UR-8200D | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-10 - Power Generation Package D
PL-004376 | PS5-60-UR-8200E | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-13 - Power Generation Package E
PL-004377 | PS5-60-UR-8200F | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-16 - Power Generation Package F
PL-004378 | PS5-60-UR-8200G | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-19 - Power Generation Package G
PL-004379 | PS5-78-JC-9100A | B | B | ROOF-final installation need to be done In PG area | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004380 | PS5-78-JC-9100B | B | B | ROOF-final installation need to be done In PG area | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004381 | PS5-78-JC-9100C | B | B | ROOF-final installation need to be done In PG area-9100 C | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004382 | PS5-78-JC-9100D | B | B | ROOF-final installation need to be done In PG area | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004384 | PS5-60-IJ-0001A-CH04 | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | Originated |  | PS5-60-01 - Power Generation Package A
PL-004385 | PS5-60-IJ-0001B-CH04 | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | Originated |  | PS5-60-04 - Power Generation Package B
PL-004386 | PS5-60-IJ-0001C-CH04 | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | Originated |  | PS5-60-07 - Power Generation Package C
PL-004387 | PS5-60-IJ-0001D-CH04 | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | Originated |  | PS5-60-10 - Power Generation Package D
PL-004388 | PS5-60-IJ-0001E-CH04 | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | Originated |  | PS5-60-13 - Power Generation Package E
PL-004389 | PS5-60-IJ-0001F-CH04 | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | Originated |  | PS5-60-16 - Power Generation Package F
PL-004390 | PS5-60-IJ-0001G-CH04 | B | E | Sand bedding not yet done , cable route marker &trench backfilled will be done after all cable installation in the trench finish | Originated |  | PS5-60-19 - Power Generation Package G
PL-004411 | PS5-78-JC-9100A | B | M | Chain to be correctly installed (still hooked on the rail). | Closed | 2026-05-02 | PS5-78-01 - Lifting and handling equipment
PL-004412 | PS5-78-JC-9100B | B | M | Chain to be installed | Closed | 2026-05-02 | PS5-78-01 - Lifting and handling equipment
PL-004413 | PS5-78-JC-9100B | B | M | Guide rail anti-derailment to be installed | Closed | 2026-05-02 | PS5-78-01 - Lifting and handling equipment
PL-004414 | PS5-78-JC-9100B | B | E | 3 pin connectors damaged for motor fan and need to be replaced --> Damage during installation | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004415 | PS5-78-JC-9100B | B | M | Control pendant height to be properly secured within the crane | Closed | 2026-05-02 | PS5-78-01 - Lifting and handling equipment
PL-004416 | PS5-78-JC-9100B | B | E | Rectify the GAP between the C/T power supply and the pendant power supply to avoid any blockage | Closed | 2026-05-02 | PS5-78-01 - Lifting and handling equipment
PL-004417 | PS5-78-JC-9100C | B | M | Guide rail anti-derailment to be installed | Closed | 2026-05-02 | PS5-78-01 - Lifting and handling equipment
PL-004418 | PS5-78-JC-9100C | B | M | Control pendant height to be properly secured within the crane | Closed | 2026-05-02 | PS5-78-01 - Lifting and handling equipment
PL-004419 | PS5-78-JC-9100D | B | E | VSD failure during testing and need to be changed by vendor (Equipment failure) | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004420 | PS5-78-JC-9100D | B | M | Damaged current collector (swapped to Crane C) to be changed | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004423 | PS5-78-JC-9100A | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004424 | PS5-78-JC-9100B | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004425 | PS5-78-JC-9100C | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004426 | PS5-78-JC-9100D | C | E | Remaining electrical work is to be completed after the installation of LV cables/ panels/ Protection cover of phase bus | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-004427 | PS5-71-UZ-6500 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-18 - Diesel Separator Module
PL-004429 | PS5-71-UZ-6700 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-004433 | PS5-71-UZ-6400 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-004436 | PS5-71-UZ-6800A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-004439 | PS5-71-UZ-6800B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-004454 | PS5-09-ACU-0007B-CG01 | A | E | PS005-E&I-M6-PL-2234 - Cable 1 side termination | Closed | 2026-07-24 | PS5-63-04 - Electrical Earthing - EITS Building
PL-004455 | PS5-09-ACU-0007A-CG01 | A | E | PS005-E&I-M6-PL-2236 - Cable 1 side termination | Closed | 2026-07-24 | PS5-63-04 - Electrical Earthing - EITS Building
PL-004456 | PS5-04-PNC-0002-CG02 | A | E | PS005-E&I-M4-PL-2238 - Cable 1 side termination | Originated |  | PS5-04-03 - 33kV ICSS System
PL-004457 | PS5-04-PNC-0001-CA64 | A | T | PS005-E&I-M4-PL-2350 - Port number (Terminal no.) N/A at interconnection drawing | Closed | 2026-03-26 | PS5-04-03 - 33kV ICSS System
PL-004458 | PS5-08-23AN-0004-CV01 | A | T | PS005-E&I-ALL-PL-2559 - Coaxial cable to be tested | Originated |  | PS5-08-23 - VHF Trunk Radio System
PL-004459 | PS5-08-23AN-1001-CV01 | A | T | PS005-E&I-ALL-PL-2560 - Coaxial cable to be tested | Originated |  | PS5-08-23 - VHF Trunk Radio System
PL-004460 | PS5-08-23AN-1002-CV01 | A | T | PS005-E&I-ALL-PL-2561 - Coaxial cable to be tested | Originated |  | PS5-08-23 - VHF Trunk Radio System
PL-004546 | PS5-06-GB-0001A-CU01 | A | I | PS005-E&I-M1-PL-2592 - Cable gland for temperature cable sensor in battery room oversize ( General punch for all the buildings) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-004547 | PS5-06-GB-0001B-CU01 | A | I | PS005-E&I-M1-PL-2592 - Cable gland for temperature cable sensor in battery room oversize ( General punch for all the buildings) | Closed | 16-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-004548 | PS5-83-OB-0001 | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | Closed | 2026-07-28 | PS5-83-01 - EITS Building
PL-004549 | PS5-83-OB-0001 | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | Closed | 2026-07-28 | PS5-83-01 - EITS Building
PL-004550 | PS5-83-OB-0001 | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | Closed | 2026-07-28 | PS5-83-01 - EITS Building
PL-004551 | PS5-83-OB-0001 | A | B | PS005-E&I-M1-PL-2605 - The MCT installed in the battery room must be replaced with an Ex-rated MCT. | Closed | 2026-07-28 | PS5-83-01 - EITS Building
PL-004552 | PS5-01-UB-6100 | C | M | PS005-MEC-ALL-PL-2606 - The name tag is messy, the letters are not straight line | Closed | 24-Jul-26 | PS5-01-09 - Inergen for EITS Building
PL-004596 | PS5-83-OB-0001 | C | B | PS005-ARC-ALL-PL-2612 - Poor quality of rubber gasket installed on the doors (easy to detaches and some contamined by water) to be replaced with the proper rubber gasket for industrial grade. | Closed | 2026-09-02 | PS5-83-01 - EITS Building
PL-004605 | PS5-83-OB-0001 | B | B | PS005-E&I-ALL-PL-2609 - Earthing bonding jumpers drawing mark up to be provided. The shorted material to be provided such as earthing boss, bonding jumper 1core 70 mm2, bonding plate inclued holes and Bolt. | Closed | 2026-05-06 | PS5-83-01 - EITS Building
PL-004654 | PS5-09-PDT-0004 | B | I | PS005-E&I-COW-1827 - Pressure Differential Transmitters (PDTs) installed for the battery exhaust fans to be replaced with fit to purpose PDTs ( new complete product code 3051CD1A22A1KKSY2L4M5Q4Q8T1D0 / 7th digit = "1" for Differential Pressure Range type = –25 to +25 in H2O / (–62.16 to +62.16 mbar) | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-004655 | PS5-09-PDT-0005 | B | I | PS005-E&I-COW-1828 - Pressure Differential Transmitters (PDTs) installed for the battery exhaust fans to be replaced with fit to purpose PDTs ( new complete product code 3051CD1A22A1KKSY2L4M5Q4Q8T1D0 / 7th digit = "1" for Differential Pressure Range type = –25 to +25 in H2O / (–62.16 to +62.16 mbar) | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-004837 | PS5-60-UA-5100 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-27 - Compressed Air Starting Skid
PL-004838 | PS5-60-UA-5200 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-26 - Instrument Air Compressor Skid
PL-004839 | PS5-71-UN-7200 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-02 - CFO Allocation Metering Package
PL-004840 | PS5-01-UV-8700 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-01-05 - Foam Skid
PL-004841 | PS5-71-UZ-6200 | A | M | 10:OSD PUNCH POINTS TO BE CLOSED | Completed |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-004842 | PS5-01-UZ-6900 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-01-10 - Water Mist Package
PL-004843 | PS5-01-UK-6100 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100)
PL-004844 | PS5-71-TR-4200 | B | M | During verification of loose materials received from Velath, I have found some issues which is related to materials. Some spools received from the vendor for the Deluge system are not fabricated as per drawing. N9 The spool received is not as per the drawing(3x2 reducer and 3” flange was not welded with the spool and 2” flange welded.). | Originated |  | PS5-71-12 - CFO Service Tank
PL-004905 | PS5-04-PMC-0005-CJ01 | A | I | PS005-E&I-COW-1974 - New cable to be added | Closed | 30-Jul-26 | PS5-04-04 - 33kV PCS System
PL-004906 | PS5-04-PMC-0008-CC59 | A | I | PS005-E&I-COW-1975 - New cable to be added | Closed | 2026-08-01 | PS5-04-04 - 33kV PCS System
PL-004909 | PS5-08-13CB-1001-CA24 | A | T | PS005-E&I-COW-1978 - New cable to be added | Closed | 30-Jul-26 | PS5-08-13 - Safety Data Network (SII SP3 SAF)
PL-004910 | PS5-09-AS-0001A-CD01 | A | E | PS005-E&I-COW-1979 - Cable to be removed | Closed | 23-Jul-26 | PS5-09-05 - HVAC for EITS Building
PL-004911 | PS5-09-AS-0001B-CD01 | A | E | PS005-E&I-COW-1980 - Cable to be removed | Closed | 23-Jul-26 | PS5-09-05 - HVAC for EITS Building
PL-004912 | PS5-09-AS-0002A-CD01 | A | E | PS005-E&I-COW-1981 - Cable to be removed | Closed | 23-Jul-26 | PS5-09-05 - HVAC for EITS Building
PL-004913 | PS5-09-AS-0002B-CD01 | A | E | PS005-E&I-COW-1982 - Cable to be removed | Closed | 23-Jul-26 | PS5-09-05 - HVAC for EITS Building
PL-004914 | PS5-61-IJ-0011-CA03 | A | T | PS005-E&I-COW-1983 - New cable to be added | Closed | 2026-08-01 | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-004915 | PS5-61-IE-0003-CS03 | A | E | PS005-E&I-COW-1984 - Cable to be removed | Closed | 2026-08-01 | PS5-61-08 - Electrical Control System
PL-005182 | PS5-01-UV-8700 | B | M | Internal piping within the skid to be completed & reinstated | Originated |  | PS5-01-05 - Foam Skid
PL-005183 | PS5-01-UV-8700 | B | M | OSD points to be cleared and closed | Originated |  | PS5-01-05 - Foam Skid
PL-005184 | PS5-01-UV-8700 | C | M | Touch up painting to be completed | Originated |  | PS5-01-05 - Foam Skid
PL-005252 | PS5-53-TR-4100 | A | M | Opening of cage ladder fabricated in the wrong direction. To be corrected as per drawing (requirement) | Closed | 2026-07-04 | PS5-53-01 - Utility Water / Storage Tank
PL-005263 | PS5-60-UR-8300A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-35 - Injector Tip Cooling Module A
PL-005265 | PS5-60-UR-8300B | B | P | 10.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-36 - Injector Tip Cooling Module B
PL-005266 | PS5-60-UR-8300C | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-37 - Injector Tip Cooling Module C
PL-005267 | PS5-60-UR-8300D | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-38 - Injector Tip Cooling Module D
PL-005268 | PS5-60-UR-8300E | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-39 - Injector Tip Cooling Module E
PL-005269 | PS5-60-UR-8300F | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-40 - Injector Tip Cooling Module F
PL-005270 | PS5-60-UR-8300G | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-41 - Injector Tip Cooling Module G
PL-005299 | PS5-60-VA-5100C | B | E | 23.1: EARTHING TO BE DONE | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-005300 | PS5 - CFO AREA_Earthing | B | E | 7 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-005308 | PS5-61-IJ-0001-CH01 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Completed |  | PS5-60-01 - Power Generation Package A
PL-005309 | PS5-61-IJ-0001-CH02 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Completed |  | PS5-60-01 - Power Generation Package A
PL-005310 | PS5-61-IJ-0001-CH03 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Completed |  | PS5-60-01 - Power Generation Package A
PL-005311 | PS5-61-IJ-0001-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-04 - Power Generation Package B
PL-005312 | PS5-61-IJ-0001-CH05 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-04 - Power Generation Package B
PL-005313 | PS5-61-IJ-0001-CH06 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-04 - Power Generation Package B
PL-005314 | PS5-61-IJ-0001-CH07 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-07 - Power Generation Package C
PL-005315 | PS5-61-IJ-0001-CH08 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-07 - Power Generation Package C
PL-005318 | PS5-61-IJ-0001-CH09 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-07 - Power Generation Package C
PL-005415 | PS5-61-IJ-0001 | A | E | PS005-E&I-COW-2194 - CTs and secondary wiring are not installed in side CT Box | Completed |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-005428 | PS5-06-GU-0001-CC03 | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CC03 INSTRUMENTATION CABLE | Closed | 28-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-005429 | PS5-06-GU-0001-CC04 | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CC04 INSTRUMENTATION CABLE | Closed | 28-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-005430 | PS5-06-GU-0001-CJ01 | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CJ01 INSTRUMENTATION CABLE | Closed | 28-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-005431 | PS5-06-GU-0001-CJ02 | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-06-GU-0001-CJ02 INSTRUMENTATION CABLE | Closed | 28-Jul-26 | PS5-06-01 - AC UPS - EITS Building
PL-005432 | PS5-08-01IO-1004-CJ01 | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-08-01IO-1004-CJ01 (HOLD) INSTRUMENTATION CABLE | Closed | 2026-08-05 | PS5-08-13 - Safety Data Network (SII SP3 SAF)
PL-005479 | PS5-61-IJ-0001-CH10 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-10 - Power Generation Package D
PL-005480 | PS5-61-IJ-0001-CH11 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-10 - Power Generation Package D
PL-005481 | PS5-61-IJ-0001-CH12 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-10 - Power Generation Package D
PL-005484 | PS5-74-UB-5100 | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-74-01 - N2 Generation Skid
PL-005485 | PS5-61-IJ-0001-CH13 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-13 - Power Generation Package E
PL-005487 | PS5-74-UB-5100 | A | M | 10.1: BROKEN SPOOL TO BE REPLACED | Closed | 2026-07-04 | PS5-74-01 - N2 Generation Skid
PL-005488 | PS5-61-IJ-0001-CH14 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-13 - Power Generation Package E
PL-005489 | PS5-61-IJ-0001-CH15 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-13 - Power Generation Package E
PL-005490 | PS5-61-IJ-0001-CH16 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-16 - Power Generation Package F
PL-005491 | PS5-61-IJ-0001-CH17 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-16 - Power Generation Package F
PL-005492 | PS5-61-IJ-0001-CH18 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-16 - Power Generation Package F
PL-005493 | PS5-61-IJ-0001-CH19 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-19 - Power Generation Package G
PL-005494 | PS5-61-IJ-0001-CH20 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-19 - Power Generation Package G
PL-005495 | PS5-61-IJ-0001-CH21 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-60-19 - Power Generation Package G
PL-005535 | PS5-25-DM-3100A-CH01 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-005536 | PS5-25-DM-3100A-CH02 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-005537 | PS5-25-DM-3100A-CH03 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-005538 | PS5-25-DM-3100A-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-005539 | PS5-25-DM-3100A-CH05 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-005540 | PS5-25-DM-3100A-CH06 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-005541 | PS5-25-DM-3100B-CH01 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-005542 | PS5-25-DM-3100B-CH02 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-005543 | PS5-25-DM-3100B-CH03 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-005545 | PS5-28-PA-3600A | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | Originated |  | PS5-28-08 - Open Drain Sump and Pumps
PL-005546 | PS5-28-PA-3600B | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | Originated |  | PS5-28-08 - Open Drain Sump and Pumps
PL-005547 | PS5-28-PA-3500 | A | M | CPP USE 15W40 FOR BEARING LUBRICATION INSTEAD OF vg32 | Originated |  | PS5-28-08 - Open Drain Sump and Pumps
PL-005558 | PS5-25-DM-3100B-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-005559 | PS5-25-DM-3100B-CH05 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-005560 | PS5-25-DM-3100B-CH06 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-005561 | PS5-25-DM-3100C-CH01 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-005562 | PS5-25-DM-3100C-CH02 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-005563 | PS5-25-DM-3100C-CH03 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-005564 | PS5-25-DM-3100C-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-005565 | PS5-25-DM-3100C-CH05 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-005566 | PS5-25-DM-3100C-CH06 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-005571 | PS5-83-OB-0001_Installation | A | E | Leveling and cleaning of the floor and cable trays/ladders | Originated |  | PS5-83-01 - EITS Building
PL-005572 | PS5-83-OB-0001_Installation | B | E | Corrosion need to be removed | Originated |  | PS5-83-01 - EITS Building
PL-005574 | PS5-83-OB-0001_Installation | A | E | Hold down Clamp not Installed yet | Originated |  | PS5-83-01 - EITS Building
PL-005575 | PS5-83-OB-0001_Installation | B | E | Earth jumper not installed completely | Originated |  | PS5-83-01 - EITS Building
PL-005751 | PS5-09-LB-0001 | B | H | PS005-E&I-ALL-PL-2596 - HVAC UCP is unable to read PDT-0004/0005 value correctly dut to oversized scale 0-300psi. (current value: High: 62210 Pa, Low:-62210Pa, Low alarm: 50 Pa) | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-005752 | PS5-09-LB-0001 | B | H | PS005-HVA-ALL-PL-2595 - Temporary banner for "Force run time" to be deleted | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-005753 | PS5-09-LB-0001 | B | H | PS005-HVA-ALL-PL-2597 - The latested PLC program to be implemented and to be performed demonstration on site | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-005754 | PS5-09-LB-0001 | B | H | PS005-HVA-ALL-PL-2599 - TSH alarm tag to be provided | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-005755 | PS5-09-LB-0001 | B | H | PS005-HVA-ALL-PL-2600 - Extract Fan PDT-0003/0004 High / Low Set point to be validated and set accordingly | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-005756 | PS5-09-LB-0001 | B | H | PS005-HVA-ALL-PL-2602 - HVAC UCP Heater function to be demonstrated (2.3 Pre iFAT Power up tests and checks) | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-005769 | PS5-28-VK-1200 | B | M | 4:The relief drum tag number is not correct to be rectified(Required PS5-28-VK-1200 but received as PS4-28-VK-1200) | Closed | 2026-07-09 | PS5-28-06 - Relief Drum and Pump
PL-006055 | PS5-61-IK-0003-CG07 | A | E | Cable to be connected | Closed | 07-Jun-26 | PS5-05-01 - Emergency Diesel Generator Package
PL-006056 | PS5-25-ESDV-0021-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-01 - Export Pipeline Pig Receiver
PL-006058 | PS5-25-ESDV-0023-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-07 - Export Pipeline Pig Launcher
PL-006061 | PS5-25-FCV-0003A-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-02 - Crude Oil Export Pump A
PL-006062 | PS5-25-FCV-0003B-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-03 - Crude Oil Export Pump B
PL-006063 | PS5-25-FCV-0003C-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-04 - Crude Oil Export Pump C
PL-006064 | PS5-25-SDV-0054A-CL01 | A | E | Cable to be connected . | Closed | 2026-06-14 | PS5-25-02 - Crude Oil Export Pump A
PL-006065 | PS5-25-SDV-0054B-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-03 - Crude Oil Export Pump B
PL-006066 | PS5-25-SDV-0054C-CL01 | A | E | Cable to be connected | Closed | 2026-06-08 | PS5-25-04 - Crude Oil Export Pump C
PL-006067 | PS5-28-SDV-0053A-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-28-13 - Seal Oil Drain Drum & Pump A
PL-006068 | PS5-61-IK-0006-CL19 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006069 | PS5-61-IK-0006-CL20 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006070 | PS5-61-IK-0006-CL21 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006071 | PS5-61-IK-0006-CL22 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006072 | PS5-62-IE-0001-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001
PL-006073 | PS5-71-HE-2400A-CL01 | A | E | Cable to be connected . | Closed | 2026-06-14 | PS5-71-01 - CFO Storage Tank Feed Heater
PL-006074 | PS5-71-HE-2400A-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-01 - CFO Storage Tank Feed Heater
PL-006090 | PS5-25-DM-3100A-CD01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-02 - Crude Oil Export Pump A
PL-006091 | PS5-25-DM-3100B-CD01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-03 - Crude Oil Export Pump B
PL-006092 | PS5-25-DM-3100C-CD01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-04 - Crude Oil Export Pump C
PL-006093 | PS5-62-IE-0001-CD01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001
PL-006094 | PS5-61-IDH-3100A-CD03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-02 - Crude Oil Export Pump A
PL-006097 | PS5-61-IDH-3100B-CD03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-03 - Crude Oil Export Pump B
PL-006100 | PS5-61-IDH-3100C-CD03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-04 - Crude Oil Export Pump C
PL-006142 | PS5-71-TR-4200 | A | M | Platform structure middle member of cfo service tank is not matching with gratings and connected drawing. To be modified | Closed | 2026-07-04 | PS5-71-12 - CFO Service Tank
PL-006193 | PS5-25-DM-3100B-CG01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-03 - Crude Oil Export Pump B
PL-006215 | PS5-61-IJ-0001 | B | E | PS005-E&I-COW-1126 - ALL CUBICLES: FINAL PROTECTION SETTINGS ARE NOT SET. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006253 | PS5-61-IK-0001 | B | E | PS005-E&I-COW-1172 - INCOMERS: FINAL PROTECTION SETTINGS ARE NOT SET. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006281 | PS5-25-DM-3100B-CG02 | A | E | cable to be connected | Closed | 2026-06-14 | PS5-25-03 - Crude Oil Export Pump B
PL-006282 | PS5-25-DM-3100C-CG01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-04 - Crude Oil Export Pump C
PL-006283 | PS5-60-TCV-0001A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-70 - Engine A Cooling system
PL-006284 | PS5-60-TCV-0001A | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-70 - Engine A Cooling system
PL-006285 | PS5-60-TCV-0001B | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-60-71 - Engine B Cooling system
PL-006286 | PS5-60-TCV-0001B | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-71 - Engine B Cooling system
PL-006287 | PS5-60-TCV-0001D | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-60-73 - Engine D Cooling system
PL-006288 | PS5-60-TCV-0001D | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-73 - Engine D Cooling system
PL-006289 | PS5-60-TCV-0001F | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-75 - Engine F Cooling system
PL-006290 | PS5-60-TCV-0001F | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-006291 | PS5-60-TCV-0001G | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-76 - Engine G Cooling system
PL-006292 | PS5-60-TCV-0001G | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-006293 | PS5-60-TCV-0002A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-70 - Engine A Cooling system
PL-006294 | PS5-60-TCV-0002A | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-70 - Engine A Cooling system
PL-006295 | PS5-60-TCV-0002B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-71 - Engine B Cooling system
PL-006296 | PS5-60-TCV-0002B | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Completed |  | PS5-60-71 - Engine B Cooling system
PL-006297 | PS5-60-TCV-0002C | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-72 - Engine C Cooling system
PL-006298 | PS5-60-TCV-0002C | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-72 - Engine C Cooling system
PL-006299 | PS5-60-TCV-0002D | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-60-73 - Engine D Cooling system
PL-006300 | PS5-60-TCV-0002D | C | M | 10.1:touch up painting to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-006301 | PS5-60-TCV-0002E | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-74 - Engine E Cooling system
PL-006302 | PS5-60-TCV-0002E | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-006303 | PS5-60-TCV-0002F | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-75 - Engine F Cooling system
PL-006304 | PS5-60-TCV-0002F | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-006305 | PS5-60-TCV-0002G | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-76 - Engine G Cooling system
PL-006306 | PS5-60-TCV-0002G | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-006313 | PS5-25-DM-3100C-CG02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-04 - Crude Oil Export Pump C
PL-006314 | PS5-79-BH-0002-CH01 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-006315 | PS5-79-BH-0002-CH02 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-006316 | PS5-79-BH-0002-CH03 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-006317 | PS5-04-PMC-0001 | A | B | PS005-E&I-M4-PL-1286 - Terminal to be update on termination drawing by enginnering (mark up drawing) (PS5-04-PMC-0001-CS01) | Closed | 2026-05-19 | PS5-04-04 - 33kV PCS System
PL-006318 | PS5-09-ACU-0007B-CD02 | A | E | PS005-E&I-M4-PL-2369 - Cable One Side Termination (COW) | Closed | 2026-07-24 | PS5-09-05 - HVAC for EITS Building
PL-006332 |  | B | E | PS005-E&I-COW-1876 - Ensure that the battery connector is compatible with the cable’s rigidity and cross-sectional characteristics. Modify the battery interconnection cables so that the positive and negative terminals are routed from the left side of the rack. | Originated |  | PS5-06-01 - AC UPS - EITS Building
PL-006333 |  | B | E | PS005-E&I-COW-1877 - Ensure that the battery connector is compatible with the cable’s rigidity and cross-sectional characteristics. Modify the battery interconnection cables so that the positive and negative terminals are routed from the left side of the rack. | Originated |  | PS5-06-01 - AC UPS - EITS Building
PL-006391 | PS5-61-IK-0001 | B | E | PS005-E&I-COW-2175 - CUBICLE : CABLE SUPPORT MISSING AND CABLE ARRANGMENT TO BE REWORKED - PS4-61-IK-0001-C01 | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006429 | PS5-04-PMC-0003-CN01 | A | T | PS005-E&I-COW-2329 - New cable to be added | Closed | 2026-08-01 | PS5-04-04 - 33kV PCS System
PL-006430 | PS5-04-PMC-0003-CN02 | A | T | PS005-E&I-COW-2330 - New cable to be added | Closed | 2026-08-01 | PS5-04-04 - 33kV PCS System
PL-006431 | PS5-04-PSC-0001 | A | I | PS005-E&I-M3-PL-2591 - AGI NEW 4 SWITCHES TO BE INSTALLED AND WIRE | Originated |  | PS5-04-04 - 33kV PCS System
PL-006449 | PS5-08-86IO-1002-CC01 | A | I | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-08-86IO-1002-CC01 (HOLD) INSTRUMENTATION CABLE | Closed | 2026-08-05 | PS5-08-15 - Security Data Network (SII SP3 SEC)
PL-006450 | PS5-09-ACU-0007A-CP01 | A | E | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-09-ACU-0007A-CP01 POWER CABLE | Closed | 2026-07-25 | PS5-09-05 - HVAC for EITS Building
PL-006451 | PS5-09-ACU-0007B-CP01 | A | E | PS005-E&I-ALL-PL-2611 - Remaining ITR to be Completed at Site as per list : PS5-09-ACU-0007B-CP01 POWER CABLE | Closed | 2026-07-25 | PS5-09-05 - HVAC for EITS Building
PL-006488 | PS5-61-IK-0003-CL13 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006489 | PS5-61-IK-0003-CL14 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006490 | PS5-61-IK-0003-CL15 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006491 | PS5-61-IK-0003-CL16 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006492 | PS5-61-IK-0003-CL17 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006493 | PS5-61-IK-0003-CL36 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006494 | PS5-61-IK-0003-CL18 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006495 | PS5-61-IK-0003-CL35 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006496 | PS5-61-IK-0003-CL34 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006497 | PS5-61-IK-0003-CL19 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006498 | PS5-61-IK-0003-CL20 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006499 | PS5-61-IK-0003-CL33 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006500 | PS5-61-IK-0003-CL32 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006501 | PS5-61-IK-0003-CL21 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006502 | PS5-61-IK-0003-CL31 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006503 | PS5-61-IK-0003-CL22 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006504 | PS5-61-IK-0003-CL30 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006505 | PS5-61-IK-0003-CL23 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006506 | PS5-61-IK-0006-CL10 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006507 | PS5-61-IK-0003-CL24 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006508 | PS5-61-IK-0006-CL11 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006509 | PS5-61-IK-0006-CL12 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006510 | PS5-61-IK-0006-CL13 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006512 | PS5-61-IK-0006-CL16 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006513 | PS5-61-IK-0006-CL17 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006514 | PS5-61-IK-0006-CL18 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006515 | PS5-61-IK-0006-CL14 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006516 | PS5-61-IK-0006-CL15 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006559 | PS5-61-IV-0002A | B | M | 4:Quality of welding in the transformer is not upto the standard. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006560 | PS5-61-IV-0002A | B | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006561 | PS5-61-IV-0002A | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006562 | PS5-61-IV-0002A | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006563 | PS5-61-IV-0002A | A | E | 4.4:Flexible conduit routing over the enclosure is improperly installed or broken | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006564 | PS5-61-IV-0002A | B | E | 4.5:Earthing cable not connected, poor cable management, improper stripping, and improper glanding | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006565 | PS5-61-IV-0002A | B | E | 4.6:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006566 | PS5-61-IV-0002A | B | E | 4.7:The opening has been temporarily sealed using plastic tape. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006567 | PS5-61-IV-0002A | A | E | 4.8:Flexible conduit not properly terminated into the cable gland. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006568 | PS5-61-IV-0002A | A | E | 4.9:All cable entries are not properly tightened and cables are not properly sealed in cable glands. Applicable for all transformers. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006569 | PS5-61-IV-0002A | A | E | 4.10:64. No heat-shrink sleeves are installed on the cable inside the main panel. Applicable for all transformers. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006570 | PS5-61-IV-0002A | A | E | 4.11:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). Applicable for all transformers. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006571 | PS5-61-IV-0002A | B | E | 4.12: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. Applicable for all transformers. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006572 | PS5-61-IV-0002A | B | E | 4.13:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc) | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006573 | PS5-61-IV-0002A | A | E | 4.14:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006574 | PS5-61-IV-0002A | B | E | 4.15:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006576 | PS5-61-IV-0002B | B | M | 4:Quality of welding in the transformer is not upto the standard. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006577 | PS5-61-IV-0002B | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006578 | PS5-61-IV-0002B | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006579 | PS5-61-IV-0002B | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006580 | PS5-61-IV-0002B | B | E | 4.4:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006581 | PS5-61-IV-0002B | B | E | 4.5:The opening has been temporarily sealed using plastic tape. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006582 | PS5-61-IV-0002B | A | E | 4.6:Cable entry is improperly installed. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006583 | PS5-61-IV-0002B | A | E | 4.7:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006584 | PS5-61-IV-0002B | A | E | 4.8:64. No heat-shrink sleeves are installed on the cable inside the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006585 | PS5-61-IV-0002B | B | E | 4.9:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006586 | PS5-61-IV-0002B | B | E | 4.10: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006587 | PS5-61-IV-0002B | B | E | 4.11:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006588 | PS5-61-IV-0002B | A | E | 4.12:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006590 | PS5-61-IV-0002B | A | E | 4.13:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006591 | PS5-61-IV-0007A | B | M | 4:Quality of welding in the transformer is not upto the standard. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006592 | PS5-61-IV-0007A | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006593 | PS5-61-IV-0007A | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006594 | PS5-61-IV-0007A | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006595 | PS5-61-IV-0007A | B | E | 4.4:Improper termination of earthing conductor | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006596 | PS5-61-IV-0007A | A | E | 4.5:Earthing cable not connected, poor cable management, improper stripping, and improper glanding. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006597 | PS5-61-IV-0007A | A | E | 4.6:Improper installation of copper bonding/earthing strap | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006598 | PS5-61-IV-0007A | B | E | 4.7:Unused gland plate sealed with rubber instead of stopping plug. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006599 | PS5-61-IV-0007A | B | E | 4.8:The opening has been temporarily sealed using plastic tape | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006600 | PS5-61-IV-0007A | A | E | 4.9:Cable entry at the bottom of the enclosure is improperly installed. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006601 | PS5-61-IV-0007A | A | M | 4.10:Oil Leakage found at the oil level gauge weld area. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006602 | PS5-61-IV-0007A | A | E | 4.11:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006603 | PS5-61-IV-0007A | A | M | 4.12:64. No heat-shrink sleeves are installed on the cable inside the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006604 | PS5-61-IV-0007A | B | M | 4.13:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006605 | PS5-61-IV-0007A | B | E | 4.14: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006606 | PS5-61-IV-0007A | B | E | 4.15:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006607 | PS5-61-IV-0007A | A | E | 4.16:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006608 | PS5-61-IV-0007A | A | E | 4.17:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006609 | PS5-61-IV-0007B | B | M | 4:Quality of welding in the transformer is not upto the standard. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006610 | PS5-61-IV-0007B | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006611 | PS5-61-IV-0007B | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006612 | PS5-61-IV-0007B | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006613 | PS5-61-IV-0007B | A | M | 4.4:Temperature sensor not sealed properly | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006614 | PS5-61-IV-0007B | B | E | 4.5:loose bolt for 1U & 1W. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006615 | PS5-61-IV-0007B | A | M | 4.6:Internal wiring and cable entry inside the enclosure are poorly installed and not properly managed, unused openings are covered by rubber plugs | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006616 | PS5-61-IV-0007B | B | E | 4.7:Unused gland plate sealed with rubber instead of stopping plug | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006617 | PS5-61-IV-0007B | A | E | 4.8:Cable entry is improperly installed. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006618 | PS5-61-IV-0007B | A | M | 4.9:Oil Leakage found at the weld area. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006619 | PS5-61-IV-0007B | A | E | 4.10:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006620 | PS5-61-IV-0007B | A | E | 4.11:64. No heat-shrink sleeves are installed on the cable inside the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006621 | PS5-61-IV-0007B | B | E | 4.12:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006622 | PS5-61-IV-0007B | B | E | 4.13: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006623 | PS5-61-IV-0007B | B | M | 4.14:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006624 | PS5-61-IV-0007B | A | E | 4.15:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006625 | PS5-61-IV-0007B | A | E | 4.16:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006626 | PS5-61-IV-0001A | B | M | 4:Quality of welding in the transformer is not upto the standard. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006627 | PS5-61-IV-0001A | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006628 | PS5-61-IV-0001A | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006629 | PS5-61-IV-0001A | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006630 | PS5-61-IV-0001A | B | M | 4.4:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006631 | PS5-61-IV-0001A | A | E | 4.5:Cable entry is improperly installed. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006632 | PS5-61-IV-0001A | B | E | 4.6:Unused gland plate sealed with rubber instead of stopping plug. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006633 | PS5-61-IV-0001A | B | E | 4.7:loose bolt for 1W. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006634 | PS5-61-IV-0001A | B | E | 4.8:Poor cable management, improper stripping and glanding. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006635 | PS5-61-IV-0001A | A | E | 4.9:Cable glanding not properly tightened and sealed | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006636 | PS5-61-IV-0001A | B | E | 4.10:Cable entry temporarily sealed using plastic tape | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006637 | PS5-61-IV-0001A | A | E | 4.11:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006638 | PS5-61-IV-0001A | A | M | 4.12:64. No heat-shrink sleeves are installed on the cable inside the main panel. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006639 | PS5-61-IV-0001A | B | E | 4.13:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006640 | PS5-61-IV-0001A | B | E | 4.14: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006641 | PS5-61-IV-0001A | B | E | 4.15:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006642 | PS5-61-IV-0001A | A | E | 4.16:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006643 | PS5-61-IV-0001A | A | E | 4.17:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006653 | PS5-61-IV-0001B | B | M | 4:Quality of welding in the transformer is not upto the standard. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006655 | PS5-61-IV-0001B | C | M | 4.1:It was found that one side has CS bolts without coating and the other side has GI bolts | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006656 | PS5-61-IV-0001B | B | M | 4.2:The coating quality is poor, with uneven surface finish, improper application, and paint peeling observed. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006657 | PS5-61-IV-0001B | B | M | 4.3:The foundation clamp for the transformer should be bolted on the transformer as well as base as per drawing. But it is welded on transformer. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006658 | PS5-61-IV-0001B | A | M | 4.4:Oil Leakage found at the oil level gauge weld area. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006659 | PS5-61-IV-0001B | A | M | 4.5:Oil Leakage found at the weld area. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006660 | PS5-61-IV-0001B | A | M | 4.6:Oil Leakage found. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006661 | PS5-61-IV-0001B | A | M | 4.7:Oil Leakage found at the weld area. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006662 | PS5-61-IV-0001B | A | M | 4.8:Oil Leakage found at the weld area. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006663 | PS5-61-IV-0001B | A | E | 4.9:internal wiring and cable entry inside the enclosure are poorly installed and not properly managed; unused openings are covered with rubber plugs | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006664 | PS5-61-IV-0001B | B | E | 4.10:poor cable management, improper stripping, and improper glanding | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006665 | PS5-61-IV-0001B | A | E | 4.11:flexible conduit routing over the enclosure is improperly installed. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006666 | PS5-61-IV-0001B | B | E | 4.12:unused gland plate is sealed with rubber instead of a stopping plug. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006667 | PS5-61-IV-0001B | A | E | 4.13:cable entry at the bottom of the enclosure is improperly installed. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006668 | PS5-61-IV-0001B | A | E | 4.14:temperature sensor is not properly sealed. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006669 | PS5-61-IV-0001B | A | E | 4.15:All cable entries are not properly tightened and cables are not properly sealed in cable glands.. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006670 | PS5-61-IV-0001B | A | E | 4.16:64. No heat-shrink sleeves are installed on the cable inside the main panel. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006671 | PS5-61-IV-0001B | B | E | 4.17:65. Rubber blind plugs on the main panels and equipment on the transformer to be changed to the proper ones (IP and Ex rate wise). | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006672 | PS5-61-IV-0001B | B | E | 4.18: Self adhesive tape to be removed and proper consumables need to be installed to provide correct installation of metal protection sleeves on the cable glands. . | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006673 | PS5-61-IV-0001B | B | E | 4.19:There is no tag plate on the main panel that need to show the characteristics of the panel (manufacturer / voltage / IP&Ex rate etc).. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006674 | PS5-61-IV-0001B | A | E | 4.20:Grounding wires are cut on the incoming/outgoing cables inside the main panel. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006675 | PS5-61-IV-0001B | A | E | 4.21:Incoming cable from temperature sensors are not properly sealed at the entry point into the main panel. | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006681 | PS5-61-IK-0003-CL41 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006683 | PS5-61-IK-0003-CL42 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006685 | PS5-61-IK-0006-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006691 | PS5-03-SFMC-0012-CD01 (Reconnection) | B | E | core 5,6,7,8 as spare to be terminated to PE at PS5-03-SFMC-0012 side | Closed | 2026-08-05 | PS5-04-05 - 33kV SIS/FGS System
PL-006692 | PS5-09-ACU-0007A-CP01 | B | E | To be installed cable tray for cable laying at PS5-09-ACU-0007A to protecting that cable from damage | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-006693 | PS5-03-SFMC-0005-CC01 | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC01/TBA08/3/PR02/WH, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006694 | PS5-61-IK-0006-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006695 | PS5-61-IK-0006-CL03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006697 | PS5-61-IK-0006-CL05 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006698 | PS5-03-SFMC-0005-CC01 | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC02/TBA09/3/PR02/WH, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006699 | PS5-61-IK-0006-CL06 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006700 | PS5-03-SFMC-0005-CC03 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC03/TBA10/4/PR02/BK, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006701 | PS5-61-IK-0006-CL07 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006702 | PS5-03-SFMC-0005-CC05 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC05/TBA12/1/PR01/WH ; /2/PR01/WH and /3/PR02/BK, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006703 | PS5-03-SFMC-0005-CC06 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC06/TBA13/1/PR01/WH ; to be replaced wire marker PS5-03-SFMC-0005-CC06/TBA13/2/PR01/BK, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006704 | PS5-03-SFMC-0005-CC07 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC07/TBA14/1/PR01/WH, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006705 | PS5-61-IK-0006-CL08 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006706 | PS5-03-SFMC-0005-CC08 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC08/TBA15/1/PR01/WH, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006707 | PS5-03-SFMC-0005-CC09 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC09/TBA16/1/PR01/WH, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006708 | PS5-03-SFMC-0005-CC18 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC18/TBA01/1/PR01/WH and /3/PR02/WH, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006709 | PS5-03-SFMC-0005-CC19 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA03 to be changed, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006710 | PS5-61-IK-0006-CL09 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006711 | PS5-03-SFMC-0005-CC20 (Reconnection) | A | I | to be changed ferulle of PS5-03-SFMC-0005-CC20/TBA06/1/PR01/WH, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006741 | PS5-61-IK-0003-CL07 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006748 | PS5-61-IK-0003-CL12 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006754 | PS5-61-IK-0003-CL08 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006755 | PS5-61-IK-0003-CL11 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006759 | PS5-61-IK-0003-CL09 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006760 | PS5-61-IK-0003-CL10 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006761 | PS5-03-SFMC-0005-CC23 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA02 to be changed, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006762 | PS5-61-IK-0003-CL37 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006764 | PS5-61-IK-0003-CL38 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006765 | PS5-61-IK-0003-CL39 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006766 | PS5-03-SFMC-0005-CC24 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA05 to be changed, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006767 | PS5-03-SFMC-0005-CC27 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD11 to be changed, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006772 | PS5-03-SFMC-0005-CC32 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD10 to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006776 | PS5-03-SFMC-0005-CC34 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD06 to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006777 | PS5-61-IK-0003-CL40 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-006780 | PS5-03-SFMC-0005-CC41 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBA07 to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006781 | PS5-03-SFMC-0006-CC01 (Reconnection) | A | I | Ferulle for PS5-03-SFMC-0006-CC01/TBD09/1/PR01/WH to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006785 | PS5-03-SFMC-0006-CC02 (Reconnection) | A | I | Ferulle for PS5-03-SFMC-0006-CC02/TBD10/3/PR02/WH to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-05 - 33kV SIS/FGS System
PL-006787 | PS5-61-IK-0003-CL43 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006790 | PS5-04-PMC-0008-CC07 (Reconnection) | A | I | All ferulles on PS5-04-PMC-0008-CC07/TBD15 to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006791 | PS5-04-PMC-0008-CC26 (Reconnection) | A | I | Core marker for PS5-04-PMC-0008-CC26/TBA12/1/PR01/WH to be installed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006792 | PS5-04-PMC-0008-CC30 (Reconnection) | A | I | Core marker for PS5-04-PMC-0008-CC30/TBD23/4/PR01/BK to be installed | Closed | 09-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006793 | PS5-61-IK-0003-CL45 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006794 | PS5-04-PMC-0008-CC39 (Reconnection) | B | I | Terminal Blok Name TBA16/04-PMC-0008-CC39 to be installed | Originated |  | PS5-04-04 - 33kV PCS System
PL-006795 | PS5-04-PMC-0008-CC40 (Reconnection) | A | I | All ferrules on PS5-04-PMC-0008-CC40/TBD25 to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006796 | PS5-04-PMC-0008-CC41 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC41/TBD08/1/PR01/WH to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006797 | PS5-61-IK-0003-CL46 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006798 | PS5-61-IK-0003-CL47 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006799 | PS5-61-IK-0003-CL48 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006801 | PS5-61-IK-0003-CL50 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006809 | PS5-61-IK-0003-CL51 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006810 | PS5-61-IK-0001-CL01 | B | E | Cable dressing not completed at both ends | Completed |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006811 | PS5-61-IK-0003-CL52 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006812 | PS5-61-IK-0001-CL01 | B | E | Trench backfilled at Transformer side without installation of Red Protection Tiles and Warning Tape over LV Power Cable | Completed |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-006813 | PS5-61-IK-0003-CL53 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006832 | PS5-04-PMC-0008-CC12 (Reconnection) | A | I | All ferulles on PS5-04-PMC-0008-CC12/TBD18 to be changed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006834 | PS5-04-PMC-0008-CC25 (Reconnection) | A | I | All ferulles on PS5-04-PMC-0008-CC25/TBA11 to be changed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006861 | PS5-04-PMC-0008-CC24 (Reconnection) | B | I | Ferulle for PS5-04-PMC-0008-CC24/TBA07/4/PR02/BK to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006862 | PS5-61-IK-0003-CL54 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006863 | PS5-04-PMC-0008-CC20 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC20/TBD07/1/PR01/WH to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006864 | PS5-04-PMC-0008-CC28 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC28/TBD21/1/PR01/WH and PS5-04-PMC-0008-CC28/TBD21/2/PR01/BK to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006865 | PS5-04-PMC-0008-CC31 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC31/TBD24/1/PR01/WH and PS5-04-PMC-0008-CC31/TBD24/2/PR01/BK to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006866 | PS5-04-PMC-0008-CC17 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC17/TBA09/1/PR01/WH and PS5-04-PMC-0008-CC17/TBA09/2/PR01/BK to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006867 | PS5-04-PMC-0008-CC13 (Reconnection) | B | I | Ferulle for PS5-04-PMC-0008-CC13/TBD19/4/PR02/BK to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006868 | PS5-04-PMC-0008-CC11 (Reconnection) | B | I | Ferulle for PS5-04-PMC-0008-CC11/TBD17/3/PR02/WH and PS5-04-PMC-0008-CC11/TBD17/4/PR02/BK to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006869 | PS5-04-PMC-0008-CC10 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC10/TBD16/1/PR01/WH to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006870 | PS5-04-PMC-0008-CC09 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC09/TBA02/1/PR01/WH to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006871 | PS5-04-PMC-0008-CC47 (Reconnection) | A | I | Ferulle for PS5-04-PMC-0008-CC47/TBA18/1/PR01/WH and PS5-04-PMC-0008-CC47/TBA18/4/PR02/BK to be changed, wire exposed | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006872 | PS5-09-PDT-0004-CJ01 (Reconnection) | B | I | Missing terminal block name XAI inside Panel PS5-09-LB-0001, to be provided | Closed | 2026-09-02 | PS5-09-05 - HVAC for EITS Building
PL-006873 | PS5-04-PMC-0002-CS03 (Reconnection) | A | E | Wrong core marker at Panel PS5-04-PMC-0002 side, to be replaced. PS5-04-PMC-0002-CS03,,, instead PS5-04-PMC-002-CS03,,, | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006874 | PS5-04-PMC-0008-CC48 (Reconnection) | B | I | to be changed terminal number on the drawing No. TZ-MID-68-SSF1-160014 page 288 of 952 due to actual number inside of panel is 1,2,3,4 | Originated |  | PS5-04-04 - 33kV PCS System
PL-006875 | PS5-61-IJ-0011-CD01 (Reconnection) | B | E | Terminal Blok Name XDI13 at Panel PS5-61-IE-0002 is not available, to be provided | Originated |  | PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011)
PL-006876 | PS5-04-PMC-0008-CC35 (Reconnection) | A | I | to provided core marker for PS5-04-PMC-0008-CC35/TBA10/7/PR04/WH at PS5-04-PMC-0008 side | Closed | 04-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006877 | PS5-03-SFMC-0005-CC33 (Reconnection) | A | I | All ferulles in PS5-03-SFMS-0005 at terminal TBD08 to be changed, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006878 | PS5-04-PMC-0008-CC57 (Reconnection) | B | I | Ferulle for PS5-04-PMC-0008-CC57/TBD32/3/PR02/WH and PS5-04-PMC-0008-CC57/TBD32/4/PR02/BK to be changed, wire exposed | Closed | 2026-08-05 | PS5-71-01 - CFO Storage Tank Feed Heater
PL-006879 | PS5-06-GU-0001-CC03 (Reconnection) | A | I | Ferulle for PS5-06-GU-0001-CC03/TBA01/1/PR01/WH and PS5-06-GU-0001-CC03/TBA01/1/PR01/BK to be changed, wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006880 | PS5-06-GU-0001-CC04 (Reconnection) | A | I | All ferulles at PS5-03-SFMC-0003/TBA01 to be changed,wire exposed | Closed | 2026-08-04 | PS5-04-05 - 33kV SIS/FGS System
PL-006881 | PS5-61-IJ-0001-CC01 (Reconnection) | A | I | All ferulles at PS5-04-PMC-0006/TBA05 to be changed, wire exposed | Closed | 2026-08-05 | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006882 | PS5-61-IJ-0001-CC02 (Reconnection) | A | I | All ferulles at PS5-04-PMC-0006/TBA06 to be changed,wire exposed | Closed | 2026-08-05 | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006883 | PS5-61-IJ-0001-CC03 (Reconnection) | A | I | All ferulles at PS5-04-PMC-0006/TBA07 to be changed, wire exposed | Closed | 2026-08-05 | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-006884 | PS5-61-IK-0001-CC15 (Reconnection) | A | I | to be changed ferulle for PS5-61-IK-0001-CC15/TBA02/1/PR01/WH; /3/PR02/WH and /5/PR03/WH, wire exposed | Closed | 09-Aug-26 | PS5-04-04 - 33kV PCS System
PL-006885 | PS5-61-IK-0001-CC40 (Reconnection) | A | I | to be changed ferulle for PS5-61-0001-CC40/TBD01/1/PR01/WH and PS5-61-0001-CC40/TBD01/8/PR04/BK, wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006886 | PS5-61-IK-0001-CC43 (Reconnection) | A | I | to be changed ferulle for PS5-61-0001-CC43/TBD03/1/PR01/WH ; /2/PR01/BK and PS5-61-0001-CC43/TBD02/3/PR02/WH; /4/PR02/BK , wire exposed | Closed | 2026-08-05 | PS5-04-04 - 33kV PCS System
PL-006887 | PS5-03-SFMC-0006-CC57 (Reconnection) | A | I | Ferulle for PS5-03-SFMC-0006-CC57/TBD07/1/PR01/WH and PS5-03-SFMC-0006-CC57/TBD07/4/PR02/BK to be changed, wire exposed | Closed | 2026-08-05 | PS5-71-01 - CFO Storage Tank Feed Heater
PL-006888 | PS5-03-SFMC-0006-CC45 (Reconnection) | A | I | Ferulle for PS5-03-SFMC-0006-CC45/TBD02/1/PR01/WH and PS5-03-SFMC-0006-CC45/TBD02/3/PR02/WH to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-05 - 33kV SIS/FGS System
PL-006889 | PS5-03-SFMC-0006-CC38 (Reconnection) | B | I | Ferulle for PS5-03-SFMC-0006-CC02/TBA12/4/PR02/BK to be changed, wire exposed | Closed | 2026-08-05 | PS5-04-05 - 33kV SIS/FGS System
PL-006894 | PS5-05-BE-0001-CG01 | A | E | Earth boss and Termination missing | Closed | 2026-08-15 | PS5-05-01 - Emergency Diesel Generator Package
PL-006895 | PS5-05-BE-0001-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006896 | PS5-05-BE-0001-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006897 | PS5-05-BE-0001-CL03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006898 | PS5-05-BE-0001-CL04 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006899 | PS5-05-BE-0001-CL05 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006900 | PS5-05-BE-0001-CL06 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006901 | PS5-61-IK-0003-CL56 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006903 | PS5-61-IK-0003-CL55 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006904 | PS5-05-BE-0001-CL08 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006905 | PS5-05-BE-0001-CL09 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006906 | PS5-05-BE-0001-CL11 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006907 | PS5-05-BE-0001-CL10 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-05-01 - Emergency Diesel Generator Package
PL-006926 | PS5-87-IRF-0001-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-53-01 - Utility Water / Storage Tank
PL-006927 | PS5-74-LB-5101-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-74-02 - N2 Generation Skid (UCP)
PL-006928 | PS5-71-XV-0092-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-20 - Diesel Fuel Day Tank
PL-006929 | PS5-28-SDV-0053B-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-28-14 - Seal Oil Drain Drum & Pump B
PL-006930 | PS5-28-SDV-0053C-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-28-15 - Seal Oil Drain Drum & Pump C
PL-006931 | PS5-71-XV-0090-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-12 - CFO Service Tank
PL-006932 | PS5-71-XV-0089-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-04 - CFO Storage Tank
PL-006933 | PS5-71-SDV-0039-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-12 - CFO Service Tank
PL-006934 | PS5-71-SDV-0001-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-20 - Diesel Fuel Day Tank
PL-006939 | PS5-62-IE-0002-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-62-02 - Lighting Control Panel - PS5-62-IE-0002
PL-006940 | PS5-61-IV-0007B-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006943 | PS5-71-FCV-0019-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-21 - Diesel Transfer Pump A/B
PL-006947 | PS5-61-IV-0007A-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006948 | PS5-71-FCV-0020-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-05 - CFO Transfer Pump A/B
PL-006949 | PS5-71-HE-2200-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-12 - CFO Service Tank
PL-006950 | PS5-71-LCV-4101-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-04 - CFO Storage Tank
PL-006951 | PS5-61-BI-0001-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-60-01 - Power Generation Package A
PL-006952 | PS5-61-BI-0002-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-60-04 - Power Generation Package B
PL-006953 | PS5-61-IK-0006-CL34 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006954 | PS5-71-HE-2200 | C | M | 4:During the inspection, the tag number and nameplate were not found. | Originated |  | PS5-71-12 - CFO Service Tank
PL-006955 | PS5-71-HE-2200 | C | M | 4.1:Two gaskets arrived without a packing list. | Originated |  | PS5-71-12 - CFO Service Tank
PL-006956 | PS5-71-HE-2200 | B | M | 4.2:The duplex RTD 3-wire was found improperly aligned and extending outside the heater bundle | Originated |  | PS5-71-12 - CFO Service Tank
PL-006957 | PS5-71-HE-2300 | C | M | 4:During the inspection, the tag number and nameplate were not found. | Originated |  | PS5-71-04 - CFO Storage Tank
PL-006958 | PS5-71-HE-2300 | C | M | 4.1:Two gaskets arrived without a packing list. | Originated |  | PS5-71-04 - CFO Storage Tank
PL-006959 | PS5-71-HE-2300 | B | M | 4.2:The duplex RTD 3-wire was found improperly aligned and extending outside the heater bundle | Originated |  | PS5-71-04 - CFO Storage Tank
PL-006960 | PS5-61-IK-0006-CL33 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006961 | PS5-61-IK-0006-CL28 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006962 | PS5-61-IK-0006-CL27 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006963 | PS5-61-IK-0006-CL26 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-006964 | PS5-61-BI-0007-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-60-19 - Power Generation Package G
PL-006967 | PS5-28-HE-2100-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-28-03 - Closed Drain Drum and Pump 01
PL-006968 | PS5-28-BE-0002B-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-28-17 - Reinjection Pump
PL-006969 | PS5-28-BE-0002A-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-28-17 - Reinjection Pump
PL-006970 | PS5-25-MOV-0008-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-07 - Export Pipeline Pig Launcher
PL-006971 | PS5-25-MOV-0025-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-01 - Export Pipeline Pig Receiver
PL-006972 | PS5-25-MOV-0026-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-01 - Export Pipeline Pig Receiver
PL-006973 | PS5-25-SDV-0046-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-05 - Crude Oil Export Pumps Bypass
PL-006974 | PS5-25-DM-3100A-CG01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-02 - Crude Oil Export Pump A
PL-006975 | PS5-25-DM-3100A-CG02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-02 - Crude Oil Export Pump A
PL-006976 | PS5-01-BE-0001-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100)
PL-007094 | PS5-01-FCV-0003A-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-01-02 - Fire Water Pump A
PL-007095 | PS5-61-IU-3100A-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007096 | PS5-61-IU-3100C-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007097 | PS5-61-IU-3100B-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007099 | PS5-61-IDH-3100A-CH01 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007100 | PS5-61-IDH-3100A-CH02 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007101 | PS5-61-IDH-3100A-CH03 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007102 | PS5-61-IDH-3100A-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007103 | PS5-61-IDH-3100A-CH05 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007104 | PS5-61-IDH-3100A-CH06 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007105 | PS5-61-IDH-3100A-CH07 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007106 | PS5-61-IDH-3100A-CH08 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007107 | PS5-61-IDH-3100A-CH09 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007108 | PS5-61-IDH-3100A-CH10 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007109 | PS5-61-IDH-3100A-CH11 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007110 | PS5-61-IDH-3100A-CH12 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-007111 | PS5-61-IDH-3100B-CH01 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007112 | PS5-61-IDH-3100B-CH02 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007113 | PS5-61-IDH-3100B-CH03 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007114 | PS5-61-IDH-3100B-CH04 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007115 | PS5-61-IDH-3100B-CH05 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007117 | PS5-61-IDH-3100B-CH07 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007118 | PS5-61-IDH-3100B-CH08 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007119 | PS5-61-IDH-3100B-CH09 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007120 | PS5-61-IDH-3100B-CH10 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007121 | PS5-61-IDH-3100B-CH11 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007122 | PS5-61-IDH-3100B-CH12 | A | E | Temporary cable ties to be replaced by permanent trefoil cleats once available at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-007173 | PS5-61-IK-0006-CL25 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-007176 | PS5-61-BI-0003-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-60-07 - Power Generation Package C
PL-007177 | PS5-61-BI-0004-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-60-10 - Power Generation Package D
PL-007178 | PS5-61-BI-0005-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-60-13 - Power Generation Package E
PL-007179 | PS5-61-BI-0006-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-60-16 - Power Generation Package F
PL-007180 | PS5-61-IK-0006-CL23 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-007181 | PS5-61-IK-0006-CL24 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006)
PL-007192 | PS5-06-GB-0003-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007193 | PS5-06-GB-0003-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007194 | PS5-74-LB-5101-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-74-02 - N2 Generation Skid (UCP)
PL-007195 | PS5-06-GB-0003-CL03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007196 | PS5-06-GB-0003-CL04 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007197 | PS5-06-GB-0003-CL05 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007198 | PS5-06-GB-0003-CL06 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007199 | PS5-06-IG-0004B-CL04 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007200 | PS5-06-GU-0003A-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007201 | PS5-06-GU-0003B-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007202 | PS5-06-GU-0003C-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007203 | PS5-06-IG-0004A-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007204 | PS5-06-IG-0004A-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007205 | PS5-06-IG-0004A-CL03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007206 | PS5-06-IG-0004A-CL04 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007207 | PS5-06-IG-0004B-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007211 | PS5-06-IG-0004B-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007212 | PS5-06-IG-0004B-CL03 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-06-02 - AC UPS - Power Generator Building
PL-007231 | PS5-60-TCV-0001C | C | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-72 - Engine C Cooling system
PL-007232 | PS5-60-TCV-0001C | C | M | 10.1: TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-72 - Engine C Cooling system
PL-007233 | PS5-60-TCV-0001E | C | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-74 - Engine E Cooling system
PL-007234 | PS5-60-TCV-0001E | C | M | 10.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-007305 | PS5-61-IDH-3100C-CH01 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007306 | PS5-61-IDH-3100C-CH02 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007307 | PS5-61-IDH-3100C-CH03 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007308 | PS5-61-IDH-3100C-CH04 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007309 | PS5-61-IDH-3100C-CH05 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007310 | PS5-61-IDH-3100C-CH06 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007311 | PS5-61-IDH-3100C-CH07 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007312 | PS5-61-IDH-3100C-CH08 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007313 | PS5-61-IDH-3100C-CH09 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007314 | PS5-61-IDH-3100C-CH10 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007315 | PS5-61-IDH-3100C-CH11 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007316 | PS5-61-IDH-3100C-CH12 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-007317 | PS5-61-IV-0002A-CH03 | A | E | trefoil cable cleats to be installed | Closed | 2026-08-26 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-007318 | PS5-61-IV-0002B-CH01 | A | E | trefoil cable cleats to be installed | Closed | 2026-08-26 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-007319 | PS5-61-IV-0002B-CH02 | A | E | trefoil cable cleats to be installed | Closed | 2026-08-26 | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-007333 | PS5-71-FCV-0018-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-13 - CFO Service Pump A/B
PL-007334 | PS5-71-HE-2300-CL02 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-04 - CFO Storage Tank
PL-007540 | PS5-82-UZ-8100 | A | M | 4:Nozzle flange distoration was observed on the Aerobic tank PS5-82-TR-4800 during inspection | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-007709 | PS5-25-XV-0053-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-25-05 - Crude Oil Export Pumps Bypass
PL-007710 | PS5-60-MOV-0005-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-12 - CFO Service Tank
PL-007711 | PS5-60-MOV-0006-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-12 - CFO Service Tank
PL-007713 | PS5-60-MOV-0011-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-12 - CFO Service Tank
PL-007715 | PS5-60-MOV-0012-CL01 | A | E | Cable to be connected | Closed | 2026-06-14 | PS5-71-12 - CFO Service Tank
PL-007805 | PS5-75-UI-6100 | B | M | 4:The welding quality on the skid is not up to the required standard, and cracks were observed in the weld areas throughout the skid. (All welded areas). | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007806 | PS5-75-UI-6100 | B | M | 4.1:During inspection, the U-clamp was found missing | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007807 | PS5-75-UI-6100 | B | M | 4.2:During inspection, the U-clamp was found to be improperly installed | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007808 | PS5-75-UI-6100 | B | M | 4.3:During the inspection, oil leakage was observed from the diaphragm pump. (PS5-75-PB-3200A). | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007809 | PS5-75-UI-6100 | B | M | 4.4:During the inspection, oil leakage was observed from the diaphragm pump (PS5-75-PB-3200B). | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007810 | PS5-75-UI-6100 | C | M | 4.5:As per the packing list, Canopy Tag No. 3300A & 3300B but received Tag No. 3200A & 3200B. | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007811 | PS5-75-UI-6100 | B | M | 4.6:During inspection After welding the pad plate, the vent holes were required to be sealed. but no one vent hole was didnt sealed,. | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007812 | PS5-75-UI-6100 | B | M | 4.7:During the inspection, some diaphragm pump support bolts were found loose, and some bolts were missing. (PS5-75-PB-3200A/B) | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007813 | PS5-75-UI-6100 | B | M | 4.8:During the inspection, the support bracing was found missing. | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007814 | PS5-75-UI-6100 | A | M | 4.9:"During the inspection, the diaphragm valve was found broken (PS5-75-BAV-1024)" | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007815 | PS5-75-UI-6100 | B | E | 4.10:"During Inspection, unproper Glanding Cable Gland for Cable Tag PS5-75-LIT-4202A-CJ01" | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007816 | PS5-75-UI-6100 | B | E | 4.11:SS Hanging Tagging for all General Transmitteri is Missing | Originated |  | PS5-75-02 - Biocide Injection Package
PL-007853 | PS5-61-ISR-0102 | C | E | 20: CP261 Pressure relay for main tank indicator was found without glass as manufactured from factory. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-007854 | PS5-61-ISR-0102 | B | E | 20.1: BR321 Gas collection pipe for gas sampling have small diameter compared to its coupling point on the Bucholz relay | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-008229 | PS5-25-PDIT-0034A | A | I | instrument to be replaced once the new transmitters arrive at site. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008230 | PS5-25-PDIT-0034B | A | I | instrument to be replaced once the new transmitters arrive at site. | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008231 | PS5-25-PDIT-0034C | A | I | instrument to be replaced once the new transmitters arrive at site. | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008468 |  | B | P | 18: Paint touchup to be done | Completed |  | PS5-25-01 - Export Pipeline Pig Receiver
PL-008469 |  | B | P | 18: Paint touchup to be done | Originated |  | PS5-25-07 - Export Pipeline Pig Launcher
PL-008493 | PS5-05-BE-0001 | B | E | EDG PJB - Anti-condensation heater circuit is missing | Originated |  | PS5-05-01 - Emergency Diesel Generator Package
PL-008540 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing | B | E | 4 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008548 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing | B | E | 9 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008553 | PS5 - POWER DISTRIBUTION AREA_Earthing | B | E | 5 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008564 | PS5-84-OB-0003_Earthing | B | E | 2 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008567 | PS5-84-OB-0004_Earthing | B | E | 2 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008569 | PS5 - EXPORT PUMP VSD AREA_Earthing | B | E | 7 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008570 | PS5 - LAUNCHER/RECEIVER AREA_Earthing | B | E | 10 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008571 | PS5 - EXPORT LOADING PUMP AREA_Earthing | B | E | 6 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008572 | PS5 - POWER GENERATION BUILDING AREA_Earthing | B | E | 4 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008573 | PS5 - CLOSED DRAIN DRUM AREA_Earthing | B | E | 7points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008574 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing | B | E | 20 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008591 | PS5 - CFO AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008592 | PS5 - CFO AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008593 | PS5 - CFO AREA_Earthing | C | E | Earthing chamber tag installed | Originated |  | PS5-63-01 - Electrical Earthing
PL-008600 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008601 | PS5 - CHEMICAL AND WASTE STORAGE AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008602 | PS5 - CLOSED DRAIN DRUM AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008603 | PS5 - CLOSED DRAIN DRUM AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008605 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008607 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008608 | PS5 - DIESEL FUEL STORAGE AND PUMP AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008609 | PS5 - EXPORT PUMP VSD AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008610 | PS5 - EXPORT PUMP VSD AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008611 | PS5 - EXPORT PUMP VSD AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008612 | PS5 - EXPORT LOADING PUMP AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008613 | PS5 - EXPORT LOADING PUMP AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008614 | PS5 - EXPORT LOADING PUMP AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008615 | PS5 - FENCE WEST AREA_Earthing | B | E | 10 connections are not completed | Originated |  | PS5-63-01 - Electrical Earthing
PL-008616 | PS5 - FENCE WEST AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008617 | PS5 - LAUNCHER/RECEIVER AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008618 | PS5 - LAUNCHER/RECEIVER AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008623 | PS5 - POWER DISTRIBUTION AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008624 | PS5 - POWER DISTRIBUTION AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008625 | PS5 - POWER DISTRIBUTION AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008640 | PS5 - POWER GENERATION BUILDING AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008641 | PS5 - POWER GENERATION BUILDING AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008642 | PS5 - POWER GENERATION BUILDING AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008643 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008644 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008645 | PS5 - POWER GENERATION COOLING TOWER AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008646 | PS5 - UTILITY AREA_Earthing | B | E | 4 points are not terminated | Originated |  | PS5-63-01 - Electrical Earthing
PL-008647 | PS5 - UTILITY AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008648 | PS5 - UTILITY AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008649 | PS5 - UTILITY AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008650 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing | B | E | 7 points are not terminated. | Originated |  | PS5-63-01 - Electrical Earthing
PL-008651 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008652 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008653 | PS5 - UTILITY/FIRE WATER STORAGE TANK AREA_Earthing | C | E | earthing chamber tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008654 | PS5-84-OB-0003_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008655 | PS5-84-OB-0003_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008656 | PS5-84-OB-0004_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008657 | PS5-84-OB-0004_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008658 | PS5-84-OB-0006_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008659 | PS5-84-OB-0006_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008660 | PS5-84-OB-0007_Earthing | B | E | anticorrosive grease is not applied | Originated |  | PS5-63-01 - Electrical Earthing
PL-008661 | PS5-84-OB-0007_Earthing | C | E | earthing busbar tag is missing | Originated |  | PS5-63-01 - Electrical Earthing
PL-008674 | PS5-61-IV-0001A-CH01 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-008675 | PS5-61-IV-0001A-CH02 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-008676 | PS5-61-IV-0001A-CH03 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-008677 | PS5-61-IV-0001B-CH01 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-008678 | PS5-61-IV-0001B-CH02 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-008679 | PS5-61-IV-0001B-CH03 | A | E | trefoil cable cleats to be installed | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-008773 | PS5-25-IES-3200A-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008774 | PS5-25-IES-3200A-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008775 | PS5-25-IES-3200B-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008776 | PS5-25-IES-3200B-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008780 | PS5-25-IES-3300A-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008782 | PS5-25-IES-3300A-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008787 | PS5-25-IES-3300B-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008788 | PS5-25-IES-3300B-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008793 | PS5-25-IES-3400B-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008794 | PS5-25-IES-3400B-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008795 | PS5-25-IES-6400A-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008796 | PS5-25-IES-6400A-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008797 | PS5-25-IES-6400B-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008798 | PS5-25-IES-6400B-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-008799 | PS5-25-IES-6500B-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008800 | PS5-25-IES-6500B-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008801 | PS5-25-IES-6600A-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008802 | PS5-25-IES-6600A-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008803 | PS5-25-IES-6600B-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008804 | PS5-25-IES-6600B-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008805 | PS5-25-IES-3400A-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008806 | PS5-25-IES-3400A-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-008807 | PS5-25-IES-6500A-CD01 | B | E | Cable gland earthing not yet installed | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-008808 | PS5-25-IES-6500A-CD01 | B | E | Wire dressing not yet done properly | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-009490 | PS5-82-UZ-8100 | A | E | 4.1:"During inspection, items inside the panel were found shaking. Package No. PS5-PKG-001" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009492 | PS5-82-UZ-8100 | B | E | 4.2:During inspection, keys were missing at the PLC control panel and MCC panel in Package No. PS5-PKG-001 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009493 | PS5-82-UZ-8100 | A | E | 4.3:"During inspection, as per the packing list, 3 Nos. of lighting fixtures were required, but only 2 Nos. arrived in Package No. PS5-PKG-001." | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009495 | PS5-82-UZ-8100 | B | M | 4.4:"PS5-PKG-002 Bolt and nut set 24 nos and Self tapping screw 100 pcs missing Package No PS5-PKG-002" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009496 | PS5-82-UZ-8100 | B | M | 4.5:"During inspection, 1 No. pipe with flange and 1 No. tee with flange arrived without a packing list in Package No. PS5-PKG-005." | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009497 | PS5-82-UZ-8100 | B | E | 4.6:"During inspection, the infrared suspended solid sensor was found damaged. Package No. PS5-PKG-006" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009498 | PS5-82-UZ-8100 | B | E | 4.7:During inspection, 1 No PS5-82-AIT-8101. 1no PS5-82-AIT-8103 and PS5-82-NRV-0010/0011/0014 arrived without a packing list in Package No. PS5-PKG-006. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009499 | PS5-82-UZ-8100 | C | M | 4.8:During inspection, rust was observed on the valve handle at sewage metering skid (Package no PS5-PKG-006) | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009500 | PS5-82-UZ-8100 | B | M | 4.9:"During inspection, support nuts were loose for sewage metering skid Pump support package No. PS5-PKG-006" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009501 | PS5-82-UZ-8100 | C | M | 4.10:"During inspection, rust was observed on the motor, coupling, and shaft area of Sludge Pump Skid PS-SKID-2, Pump No. PS5-82-PE-3400A/B. (Package no PS5-PKG-007)" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009502 | PS5-82-UZ-8100 | A | E | 4.11:During inspection, keys were missing at the Junction box of sludge pump skid Package No.PS5-PKG-007 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009503 | PS5-82-UZ-8100 | B | M | 4.12:During inspection, support nuts were missing for Permeate Pump PS5-82-DM-3200A/B of permeate pump skid in Package No. PS5-PKG-008 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009504 | PS5-82-UZ-8100 | A | M | 4.13:During inspection, flange bolts were found missing of permete pump skid in Package No. PS5-PKG-008 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009505 | PS5-82-UZ-8100 | B | M | 4.14:During inspection, pipe U clamp support nuts were loosen permete pump skid in Package No. PS5-PKG-008 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009506 | PS5-82-UZ-8100 | B | M | 4.15:During inspection, rust was observed on the motor wheel of roots blower skid in Package No. PS5-PKG-011 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009507 | PS5-82-UZ-8100 | B | M | 4.16:During inspection, pump support bolt nuts were found on the floor of roots blower skid.in package no.PS5-PKG-011 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009508 | PS5-82-UZ-8100 | B | M | 4.17:"During inspection, as per the packing list, 15 Nos. of operation columns , but only 1 No. arrived in Package No. PS5-PKG-023." | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009509 | PS5-82-UZ-8100 | B | M | 4.18:The welding quality on the dosing pump skid is not up to the required standard in package no PS5-PKG-017 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009511 | PS5-82-UZ-8100 | B | M | 4.19:"The welding quality on the MDR membrane module skid is not up to the required standard in package no PS5-PKG-020" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009512 | PS5-82-UZ-8100 | C | M | 4.20:During inspection, it was observed that pickling and passivation were not carried out at the MDR membrane module skid stainless welded area after welding package no PS5-PKG-020. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009513 | PS5-71-BI-1110-CC01 | B | I | No segregation between INS cables as per project specification | Originated |  | PS5-91-01 - Multicore cables & JB
PL-009514 | PS5-82-UZ-8100 | B | M | 4.21:During inspection, Dosing pump support nuts were found missing in package no. PS5-PKG-012 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009515 | PS5-82-UZ-8100 | C | M | 4.22:During inspection, rust was observed on the gratings of sludge dewatering tank in Package No. PS5-PKG-024 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009516 | PS5-82-UZ-8100 | B | M | 4.23:The welding quality on the explosion proof box is not up to the required standard in package no PS5-PKG-022 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009518 | PS5-82-UZ-8100 | B | M | 4.24:During inspection,effluent pump skid flange stud bolts were found missing, and some stud bolts were found loose in package no. PS5-PKG-010 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009519 | PS5-82-UZ-8100 | B | E | 4.25:During inspection, terminal block numbers were found missing in the junction box of Package No. PS5-PKG-008 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009521 | PS5-82-UZ-8100 | B | E | 4.26:During inspection, a plug was found missing at the junction box in Package No. PS5-PKG-008 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009522 | PS5-71-BI-1116-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009523 | PS5-82-UZ-8100 | B | E | 4.27:During inspection, the Teflon sheet was found missing at the junction box in Package No. PS5-PKG-008 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009524 | PS5-82-UZ-8100 | B | E | 4.28:During inspection, a plug was found missing at MCC Panel PS5-82-IN-0001 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009525 | PS5-71-BI-1306-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009526 | PS5-82-UZ-8100 | B | E | 4.29:During inspection, improper cable laying was observed at PS5-83-PIT-8104-CC01. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009527 | PS5-25-BI-2308-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009528 | PS5-82-UZ-8100 | B | E | 4.30:During inspection, cable stress was observed in Package No. PS5-PKG-008. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009529 | PS5-25-BI-2108-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009530 | PS5-25-BI-2315-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009531 | PS5-82-UZ-8100 | B | E | 4.31:During inspection, no bonding jumper was found in Package No. PS5-PKG-008. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009532 | PS5-25-BI-2109-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009533 | PS5-82-UZ-8100 | A | E | 4.32:During inspection, ferrules were found missing at Panel PS5-82-IN-0001 | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009534 | PS5-25-BI-2316-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009535 | PS5-25-BI-2312-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009536 | PS5-82-UZ-8100 | A | E | 4.33:"During inspection, equipment drop damage was observed in Package No. PS5-PKG-001" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009537 | PS5-25-BI-1104-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009538 | PS5-82-UZ-8100 | B | E | 4.34:"During inspection, a plug was found missing at Panel PS5-82-IN-0001" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009539 | PS5-03-BI-2502-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-03-06 - FZ-06 - Transformer Area
PL-009540 | PS5-82-UZ-8100 | B | E | 4.35:"During inspection, terminal block numbers were found missing in Panel PS5-82-IN-0001" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009541 | PS5-71-BI-2317-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-71-15 - Diesel Fuel Storage Tank
PL-009542 | PS5-82-UZ-8100 | B | E | 4.36:Cover bend was observed on Panel PS5-82-IN-0001. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009543 | PS5-25-BI-1103-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009544 | PS5-82-UZ-8100 | B | E | 4.37:During inspection, improper equipment tag installation was observed on the Ventilator Fan Selector in Package No. PS5-PKG-001) | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009545 | PS5-71-BI-2314-CC01 | B | I | No segregation between INS cables as per project specification | Completed |  | PS5-91-01 - Multicore cables & JB
PL-009546 | PS5-82-UZ-8100 | C | M | 4.38:During inspection container PS5-82-OC-0001 name board bolts 2 nos missing | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009547 | PS5-82-UZ-8100 | B | M | 4.39:"During inspection, M12 stud bolts were found missing on the mechanical screw screen support, tag no. PS5-82-MES-9100. package no. PS5-PKG-008" | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009548 | PS5-82-UZ-8100 | B | M | 4.40:During inspection, the roof sheet connecting Angle was not received. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009549 | PS5-82-UZ-8100 | B | M | 4.41:During inspection, it was found that all gaskets were improperly packed, resulting in damage to most of the gaskets. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009550 | PS5-82-UZ-8100 | A | M | 4.42:During inspection, only the sludge dewatering tank supporting structure was received. The sludge dewatering tank, tag no. PS5-82-TR-4400, was not received in package no. PS5-PKG-021. | Completed |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009551 | PS5-60-BE-0001-CL04 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-009552 | PS5-82-UZ-8100 | B | E | 4.43:As per the packing list, 100 Nos. of stainless steel bolt and nut sets, they were not received in Package No. PS-PKG-021. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009553 | PS5-61-IK-0003-CL01 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-009554 | PS5-82-UZ-8100 | B | M | 4.44:The most items of package received does not match the packing list. The items have been mixed up and packed in different packages. | Originated |  | PS5-82-02 - Sewage Treatment Plant Package
PL-009555 | PS5-61-IK-0003-CL02 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003)
PL-009557 | PS5-60-BE-0002-CL05 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-009558 | PS5-60-BE-0002-CL01 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-009559 | PS5-60-BE-0002-CL02 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-009560 | PS5-60-BE-0007A-CL01 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-009561 | PS5-60-BE-0007A-CL02 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-009562 | PS5-60-BE-0007A-CL03 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-009564 | PS5-60-BE-0007B-CL01 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-009566 | PS5-60-BE-0007B-CL02 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-009567 | PS5-60-BE-0007B-CL03 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-009568 | PS5-60-BE-0001-CL01 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-009569 | PS5-60-BE-0001-CL02 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-009570 | PS5-60-BE-0002-CL03 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-009571 | PS5-60-IE-0003A-CD15 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-01 - Power Generation Package A
PL-009572 | PS5-60-IE-0003B-CD15 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-60-04 - Power Generation Package B
PL-009573 | PS5-06-GU-0003A-CD02 | B | E | No segregation between 48VDC and 110/230/400VAC cables as per project specification. | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-009686 | PS5-63-IV-0010 | B | M | 4:During inspection, rust was found on both sides inside the radiator. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009687 | PS5-63-IV-0010 | B | M | 4.1:During inspection, rust was found on the integrated relay unit and CT trminal box bolts. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009688 | PS5-63-IV-0010 | B | M | 4.2:The welding quality on the transformer is not up to the required standard (some welded area), | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009689 | PS5-63-IV-0010 | B | M | 4.3:During inspection, only the anchor angle bolts were received. The nuts and washers were not received | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009690 | PS5-63-IV-0011 | B | M | 4:During inspection, rust was found on both sides inside the radiator. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009691 | PS5-63-IV-0011 | B | M | 4.1:During inspection, rust was found on the integrated relay unit and CT trminal box bolts. | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009692 | PS5-63-IV-0011 | B | M | 4.2:The welding quality on the transformer is not up to the required standard (some welded area), | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009693 | PS5-63-IV-0011 | B | M | 4.3:During inspection, only the anchor angle bolts were received. The nuts and washers were not received | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-009745 | PS5-60-EA-2100A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-70 - Engine A Cooling system
PL-009746 | PS5-60-EA-2100A | C | M | 10.1: Touch up / painting to be completed wherever required on the equipment | Completed |  | PS5-60-70 - Engine A Cooling system
PL-009748 | PS5-25-PA-3100A | B | M | 21 Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-009749 | PS5-25-PA-3100A | B | M | 21.1: 3/4" blind flange to be installed on the suction nozzle of pump | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-009750 | PS5-25-PA-3100A | C | M | 21.2: Insulation (Flexible jackets) to be reinstated properly | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-009751 | PS5-25-PA-3100B | B | M | 21:Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-009752 | PS5-25-PA-3100B | B | M | 21.1:3/4" blind flange to be installed on the suction nozzle of pump | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-009753 | PS5-25-PA-3100B | C | M | 21.2:Insulation (Flexible jackets) to be reinstated properly | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-009754 | PS5-25-PA-3100B | A | M | 21.3:Coupling spacer to be located and installed (Coupling received from vendor is not matching with Export pump - B , also coupling guard to be installed)) | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-009755 | PS5-25-PA-3100C | B | M | 21:Coupling spacer to be tinghtened properly after motor SOLO-RUN. (Shims are available in PS5 CPP store) | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-009756 | PS5-25-PA-3100C | B | M | 21.1:3/4" blind flange to be installed on the suction nozzle of pump | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-009757 | PS5-25-PA-3100C | C | M | 21.2:Insulation (Flexible jackets) to be reinstated properly | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-009758 | PS5-60-EA-2100B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-70 - Engine A Cooling system
PL-009759 | PS5-60-EA-2100B | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-70 - Engine A Cooling system
PL-009760 | PS5-60-EA-2200A | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-60-71 - Engine B Cooling system
PL-009761 | PS5-60-EA-2200A | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-71 - Engine B Cooling system
PL-009762 | PS5-60-EA-2200B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-71 - Engine B Cooling system
PL-009763 | PS5-60-EA-2200B | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-71 - Engine B Cooling system
PL-009764 | PS5-60-EA-2300A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-72 - Engine C Cooling system
PL-009765 | PS5-60-EA-2300A | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-72 - Engine C Cooling system
PL-009766 | PS5-60-EA-2300B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-72 - Engine C Cooling system
PL-009767 | PS5-60-EA-2300B | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-72 - Engine C Cooling system
PL-009768 | PS5-60-EA-2400A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-73 - Engine D Cooling system
PL-009769 | PS5-60-EA-2400A | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-73 - Engine D Cooling system
PL-009770 | PS5-60-EA-2400B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-73 - Engine D Cooling system
PL-009772 | PS5-60-EA-2400B | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-73 - Engine D Cooling system
PL-009773 | PS5-60-EA-2500A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping | Completed |  | PS5-60-74 - Engine E Cooling system
PL-009774 | PS5-60-EA-2500A | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-74 - Engine E Cooling system
PL-009775 | PS5-60-EA-2500B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-74 - Engine E Cooling system
PL-009776 | PS5-60-EA-2500B | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-74 - Engine E Cooling system
PL-009777 | PS5-60-EA-2600A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-75 - Engine F Cooling system
PL-009778 | PS5-60-EA-2600A | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-75 - Engine F Cooling system
PL-009779 | PS5-60-EA-2600B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-75 - Engine F Cooling system
PL-009781 | PS5-60-EA-2600B | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-75 - Engine F Cooling system
PL-009782 | PS5-60-EA-2700A | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-76 - Engine G Cooling system
PL-009783 | PS5-60-EA-2700A | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-76 - Engine G Cooling system
PL-009784 | PS5-60-EA-2700B | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-76 - Engine G Cooling system
PL-009785 | PS5-60-EA-2700B | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-76 - Engine G Cooling system
PL-009828 | PS5-25-PA-3100A | B | M | 17:Alignment to be verified while installing suction and discharge line valves. | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-009846 | PS5-25-PA-3100B | B | M | 17:Alignment to be verified while installing suction and discharge line valves | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-009847 | PS5-25-PA-3100C | B | M | 17:Alignment to be verified while installing suction and discharge line valves | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-010025 |  | B | E | Junction Box TAG is missing | Originated |  | PS5-62-09 - Outdoor Normal Lighting DB - PS5-61-IG-0007
PL-010028 |  | B | E | Junction Box TAG is missing | Originated |  | PS5-62-09 - Outdoor Normal Lighting DB - PS5-61-IG-0007
PL-010115 | PS5-28-IES-3900A-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-28-17 - Reinjection Pump
PL-010116 | PS5-71-IES-3200-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-71-14 - Diesel Fuel Transfer and Dispensing Station
PL-010120 | PS5-71-IES-3300A-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-71-05 - CFO Transfer Pump A/B
PL-010121 | PS5-71-IES-3300B-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-71-05 - CFO Transfer Pump A/B
PL-010126 | PS5-71-IES-3400A-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-71-13 - CFO Service Pump A/B
PL-010131 | PS5-71-IES-3500A-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-010132 | PS5-71-IES-3500B-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-010133 | PS5-53-IES-3100A-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-53-02 - Water Distribution Pump A/B
PL-010134 | PS5-53-IES-3100B-CD01 | B | E | Cable gland earthing is not yet installed | Originated |  | PS5-53-02 - Water Distribution Pump A/B
PL-010183 | PS5-60-TX-41100A | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-70 - Engine A Cooling system
PL-010184 | PS5-60-TX-41100A | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-70 - Engine A Cooling system
PL-010185 | PS5-60-TX-41100A | B | E | 23.2:EARTHING TO BE DONE | Originated |  | PS5-60-70 - Engine A Cooling system
PL-010186 | PS5-60-TX-41100B | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-70 - Engine A Cooling system
PL-010187 | PS5-60-TX-41100B | C | M | 23.1:Touch up / painting to be completed wherever required on the equipmen | Originated |  | PS5-60-70 - Engine A Cooling system
PL-010188 | PS5-60-TX-41100B | B | E | 23.2:EARTHING TO BE DONE | Originated |  | PS5-60-70 - Engine A Cooling system
PL-010189 | PS5-60-TX-41200A | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-71 - Engine B Cooling system
PL-010190 | PS5-60-TX-41200A | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-71 - Engine B Cooling system
PL-010191 | PS5-60-TX-41200A | B | E | 23.2: ERTHING TO BE DONE | Originated |  | PS5-60-71 - Engine B Cooling system
PL-010192 | PS5-60-TX-41200B | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-71 - Engine B Cooling system
PL-010193 | PS5-60-TX-41200B | C | M | 23.1:Touch up / painting to be completed wherever required on the equipmen | Originated |  | PS5-60-71 - Engine B Cooling system
PL-010194 | PS5-60-TX-41200B | B | E | 23.2:EARTHING TO BE DONE | Originated |  | PS5-60-71 - Engine B Cooling system
PL-010358 |  | B | P | 18:Pickling and passivation to be done | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-010360 |  | B | P | 18:Pickling and Passivation to be done | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-010385 | PS5-08-01MP-0001-CC01 | B | T | Cable not Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-010387 | PS5-08-01MP-0001-CC03 | B | T | Cable not Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-010388 | PS5-08-01MP-0001-CC04 | B | T | Cable not Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-010561 | PS5-71-PA-3500A | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-010562 | PS5-71-PA-3500A | C | M | 21.1:Touch up / painting to be completed wherever required on the equipmen | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-010563 | PS5-71-PA-3500B | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-010564 | PS5-71-PA-3500B | C | M | 21.1:Touch up / painting to be completed wherever required on the equipmen | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-010755 |  | B | P | 18:Pickling and passivation to be done | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-010756 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-010765 |  | B | P | 18: Pickling and passivation to be don | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-010766 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-010865 | PS5-05-IE-8100 | B | E | bar not connected to earth grid | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-010868 | PS5-05-IE-8100 | C | E | The Panel Frame not to be touch up paint | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-010904 |  | B | P | 18.1: RLMU to be done | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-010912 | PS5-60-LA-0002B | B | I | bar not connected to isolated earth grid | Originated |  | PS5-60-10 - Power Generation Package D
PL-010921 | PS5-60-LA-0002C | B | I | bar not connected to isolated earth grid | Originated |  | PS5-60-16 - Power Generation Package F
PL-010964 |  | B | P | 18: Paint touch up to be done | Originated |  | PS5-01-05 - Foam Skid
PL-010965 |  | B | P | 18:Pickling and passivation to be done | Originated |  | PS5-01-06 - Foam Concentrate Distribution
PL-010967 |  | B | P | 18.1:RLMU to be done | Originated |  | PS5-01-06 - Foam Concentrate Distribution
PL-010968 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-28-12 - Open Drains (OD3)
PL-011075 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011077 |  | B | P | 18:Pickling and passivation to be done | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011079 |  | B | P | 18:Paint touchup to be don | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-011080 |  | B | P | 18:Pickling and passivation to be done | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-011103 | PS5-08-01LS-0101-CR01 | B | T | Cable no Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-011108 | PS5-08-01BT-1904-CR01 | B | T | Cable no Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-011109 | PS5-08-01BT-1902-CR02 | B | T | Cable no Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-011110 | PS5-08-01BT-1903-CR01 | B | T | Cable no Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-011111 | PS5-08-01LS-0201-CR01 | B | T | Cable no Dressing at Both Ends | Originated |  | PS5-08-01 - PAGA
PL-011146 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-26 - Instrument Air Compressor Skid
PL-011147 |  | B | P | 18.1:1" ValveCTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-011148 |  | B | P | 18.2:Paint touchup to be done | Completed |  | PS5-60-26 - Instrument Air Compressor Skid
PL-011149 |  | B | P | 18:F1 flange connection to PS5-60-UA-5200/TP-311 is pending. | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-011150 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-26 - Instrument Air Compressor Skid
PL-011151 |  | B | P | 18.2:Paint touchup to be done | Completed |  | PS5-60-26 - Instrument Air Compressor Skid
PL-011152 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-27 - Compressed Air Starting Skid
PL-011153 |  | B | P | 18.1:Sleeve Penetration to be install | Completed |  | PS5-60-27 - Compressed Air Starting Skid
PL-011154 |  | B | P | 18.2:Paint touchup to be done | Completed |  | PS5-60-27 - Compressed Air Starting Skid
PL-011158 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-18 - Diesel Separator Module
PL-011159 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-71-18 - Diesel Separator Module
PL-011207 |  | B | P | 18.2:cladding penetration to be install | Completed |  | PS5-71-18 - Diesel Separator Module
PL-011209 | PS5-71-BE-0001B-CL01 | A | E | Cable is damaged | Originated |  | PS5-71-07 - Crude Fuel Separation Module (UCP)
PL-011313 |  | B | P | 18:Electrical heat tracing to be done | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-011314 |  | B | P | 18.1:Insulatoin to be done | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-011315 |  | B | P | 18.2:Paint touchup to be done | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-011317 |  | B | P | 18:Electrical heat tracing to be done | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-011318 |  | B | P | 18.1:Insulatoin to be done | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-011319 |  | B | P | 18.2:Paint touchup to be done | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-011320 |  | B | P | 18:Electrical heat tracing to be done | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-011321 |  | B | P | 18.1:Insulatoin to be done | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-011323 |  | B | P | 18.2:Paint touchup to be done | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-011328 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011330 |  | B | P | 18.1:Pickling & Passivation to be done in rusted area | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011331 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011332 |  | B | P | 18.1:Pickling & Passivation to be done in rusted area | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011333 |  | B | P | 18:Valve Commodity code RLMU to be done | Originated |  | PS5-71-02 - CFO Allocation Metering Package
PL-011334 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-71-02 - CFO Allocation Metering Package
PL-011335 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-011336 |  | B | P | 18.1:Pickling & Passivation to be done in rusted area | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-011337 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-28-07 - Open Drains (OD2)
PL-011338 |  | B | P | 18.1:Pickling & Passivation to be done in rusted area | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-011339 |  | B | P | 18.2:Pickling & Passivation to be done in rusted area | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-011340 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-011341 |  | B | P | 18.1:Pickling & Passivation to be done in rusted area | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-011342 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-011343 |  | B | P | 18.1:Pickling & Passivation to be done in rusted area | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-011344 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-74-03 - Nitrogen Receiver
PL-011345 |  | B | P | 18.1:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-74-03 - Nitrogen Receiver
PL-011346 |  | B | P | 18.2:Paint Touch up to be done | Originated |  | PS5-74-03 - Nitrogen Receiver
PL-011347 |  | B | P | 18:Paint touch up to be done | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-011348 |  | B | P | 18:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-01 - Power Generation Package A
PL-011349 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-011350 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-01 - Power Generation Package A
PL-011351 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-01 - Power Generation Package A
PL-011352 |  | B | P | 18:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011353 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011354 |  | B | P | 18.2:Pickling & passivation to be done in rusted area | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-011355 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-011356 |  | B | P | 18.1:Paint touch up to be done | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-011408 |  | B | P | 18:Hose Connection FM to be Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-011409 |  | B | P | 18.1:Wear pad support holes shall be sealed. | Completed |  | PS5-60-01 - Power Generation Package A
PL-011410 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-01 - Power Generation Package A
PL-011411 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-01 - Power Generation Package A
PL-011412 |  | B | P | 18:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-01 - Power Generation Package A
PL-011414 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-011416 |  | B | P | 18.2:Wear pad support holes shall be sealed. | Completed |  | PS5-60-01 - Power Generation Package A
PL-011418 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-01 - Power Generation Package A
PL-011419 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-01 - Power Generation Package A
PL-011420 |  | B | P | 18:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-04 - Power Generation Package B
PL-011421 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-04 - Power Generation Package B
PL-011422 |  | B | P | 18.2:Wear pad support holes shall be sealed. | Completed |  | PS5-60-04 - Power Generation Package B
PL-011423 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-04 - Power Generation Package B
PL-011424 |  | B | P | 18.4:Paint touch up to be done | Originated |  | PS5-60-04 - Power Generation Package B
PL-011425 |  | B | P | 18:Hose Connection FM to be Done | Originated |  | PS5-60-04 - Power Generation Package B
PL-011426 |  | B | P | 18.1:Wear pad support holes shall be sealed | Completed |  | PS5-60-04 - Power Generation Package B
PL-011427 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-04 - Power Generation Package B
PL-011428 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-04 - Power Generation Package B
PL-011435 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-04 - Power Generation Package B
PL-011437 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-04 - Power Generation Package B
PL-011438 |  | B | P | 18.2:Wear pad support holes shall be sealed. | Completed |  | PS5-60-04 - Power Generation Package B
PL-011440 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-04 - Power Generation Package B
PL-011441 |  | B | P | 18.4:Cladding Penetration to be Fix | Originated |  | PS5-60-04 - Power Generation Package B
PL-011443 |  | B | P | 18.5:Paint touch up to be done | Originated |  | PS5-60-04 - Power Generation Package B
PL-011447 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011448 |  | B | P | 18.1:Valve Handle missing | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011449 |  | B | P | 18.2:PR01 (PS-71493) to be install | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011450 |  | B | P | 18.3:PR01 (PS-504481) to be install | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011451 |  | B | P | 18.4:Wear pad support holes shall be sealed | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011452 |  | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011453 |  | B | P | 18.6:Cladding Penetration to be Fix | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011454 |  | B | P | 18.7:Paint touch up to be done | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011562 |  | B | P | 18:PR01 to be install | Completed |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-011563 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-011564 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-011565 |  | B | P | 18.3:Floor penetration gratings shall be fixed properly. | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-011566 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-011567 |  | B | P | 18:PR01 to be install | Completed |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011568 |  | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011569 |  | B | P | 18.2:Floor & Clading penetration gratings shall be fixed properly. | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011570 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011571 |  | B | P | 18.4:Paint touch up to be done | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011572 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011573 |  | B | P | 18.1:Floor & Clading penetration gratings shall be fixed properly. | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011574 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011575 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011601 |  | B | P | 18:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-011602 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-011604 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-35 - Injector Tip Cooling Module A
PL-011606 |  | B | P | 18.3:Floor Penetration Gratings to be Fixed | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-011607 |  | B | P | 18.4:Paint touch up to be done | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-011619 |  | B | P | 18:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-011620 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-011622 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-36 - Injector Tip Cooling Module B
PL-011623 |  | B | P | 18.3:Floor Penetration Gratings to be Fixed | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-011624 |  | B | P | 18.4:Paint touch up to be done | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-011626 |  | B | P | 18:1" ValveCTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011628 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011629 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011631 |  | B | P | 18.3:Floor Penetration Gratings to be Fixed | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011632 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-011635 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011650 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011652 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011653 |  | B | P | 18.3:Floor Penetration Gratings to be Fixed | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011654 |  | B | P | 18.4:Floor Penetration Gratings to be Fixed | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011655 |  | B | P | 18.5:Paint touch up to be done | Completed |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-011656 |  | B | P | 18:Instruments to be Install | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-011659 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-011660 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-011846 |  | B | P | 18:1" CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-011847 |  | B | P | 18.1:Hose Connection FM to be Done | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-011848 |  | B | P | 18.2:PR01 Bottom shim to be sealed. | Completed |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-011849 |  | B | P | 18.3:Floor Penetration Gratings to be Fixed. | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-011850 |  | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-011851 |  | B | P | 18.5:Paint touch up to be done | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-011852 |  | B | P | 18:Provide shim as required | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011853 |  | B | P | 18.1:PR01 (PS-58240) to be installed and sealed | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011854 |  | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011855 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011856 |  | B | P | 18.4:Through wall penetration to be Fixed. | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011857 |  | B | P | 18.5:Paint touch up to be done | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011858 |  | B | P | 18:Provide shim as required | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011859 |  | B | P | 18.1:Bottom shim to be sealed. | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011860 |  | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011861 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011862 |  | B | P | 18.4:Through wall penetration to be Fixed. | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011863 |  | B | P | 18.5:Paint touch up to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011864 |  | B | P | 18:Provide shim as required | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011865 |  | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011866 |  | B | P | 18.2:Through wall penetration to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011867 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011868 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011869 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011870 |  | B | P | 18.1:Provide shim as required | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011871 |  | B | P | 18.2:Through wall penetration to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011872 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011873 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011925 |  | B | P | 18.5: S8 GL01 (PS-61260) GAP to be verify after PTFE installed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011929 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011930 |  | B | P | 18.1:TZ-MID-68-WPR2-207040 F6 & TZ-MID-68-WPR2-207034 F5 Stud bolt protrusion is less than 2 threads | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011931 |  | B | P | 18.2:S16 (PS-61210)-GL01 gap shall be verified after PTFE pad installation | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011932 |  | B | P | 18.3:PS5-60-TX-41200A/TP-614 & TP-600, PS5-60-UR-8100B-TP-800 & TP-802 Equpiment connection Flange Management to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011933 |  | B | P | 18.4:PS5-60-TG-0006B F9 - Stud bolt protrusion is less than 2 threads | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011934 |  | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011935 |  | B | P | 18.6:Paint touch up to be done | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011936 |  | B | P | 18:Drg no TZ-MID-68-WPR2-207045 S10 (PS-61220)- GL01 gap shall be verified after PTFE pad installation | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011937 |  | B | P | 18.1:Drg No TZ-MID-68-WPR2-207045 S9 (PS-61218)-PR01 to be install | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011938 |  | B | P | 18.2:PS5-60-TG-0007B F-7 Stud bolt protrusion is less than 2 threads | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011939 |  | B | P | 18.3:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011940 |  | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011941 |  | B | P | 18.5:Paint touch up to be done | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011942 |  | B | P | 18:Drg no TZ-MID-68-WPR2-207053 S14 (PS-61239,61236,61243)- GL01 gap shall be verified after PTFE pad installation | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011943 |  | B | P | 18.1:Drg No TZ-MID-68-WPR2-207053 S13(PS-61236, 61237, 61242,61243,61244) - PR01 To be install | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011944 |  | B | P | 18.2:PS5-60-TG-0008B- F-8 Stud bolt protrusion is less than 2 threads | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011945 |  | B | P | 18.3:Drg No TZ-MID-68-WPR2-207059,S4(PS-61252)-Shoe stiffener sharp edges shall be ground smooth. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011946 |  | B | P | 18.4:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-011947 |  | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011948 |  | B | P | 18.6:Paint touch up to be done | Completed |  | PS5-60-71 - Engine B Cooling system
PL-011949 |  | B | P | 18:Drg No TZ-MID-68-WPR2-20773,F-02 -Flange Management to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011950 |  | B | P | 18.1:Drg No TZ-MID-68-WPR2-207735, S13(PS-74840)-PR01 to be install | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011951 |  | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011952 |  | B | P | 18.3:Through Wall Penetration to be Fixed. | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011953 |  | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011954 |  | B | P | 18.5:Paint touch up to be done | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011955 |  | B | P | 18:-TZ-MID-68-WPR2-208152, F2- Flange Management report to be Closed | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011956 |  | B | P | 18.1:Drg No TZ-MID-68-WPR2-208152, S14(PS-86745)- LS01 one-side gap to be adjusted | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011957 |  | B | P | 18.2:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011958 |  | B | P | 18.3:Through Wall Penetration to be Fixed. | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011959 |  | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011960 |  | B | P | 18.5:Paint touch up to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-011973 |  | B | P | 18:TZ-MID-68-WPR2-206797 F5 & TZ-MID-68-WPR2-206806F6- Stud bolt protrusion is less than 2 threads | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011974 |  | B | P | 18.1:TZ-MID-68-WPR2-206798,Item 04-Gate Valve Handle Clash With Handrail | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011979 |  | B | P | 18.2:PS5-60-TG-0006A & PS5-60-TG-0005A - Stud bolt protrusion is less than 2 threads | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011981 |  | B | P | 18.3:PS5-60-UR-8100A-TP-770 & TP-781,PS5-60-TX-41100A-TP-598- Equpiment connection joint Flange Management to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011983 |  | B | P | 18.4:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011984 |  | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011985 |  | B | P | 18.6:Paint touch up to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011986 |  | B | P | 18:S11 Drg No TZ-MID-68-WPR2-206810 (PS-51551)-GL01 gap shall be verified after PTFE pad installation | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011987 |  | B | P | 18.1:PS5-60-TG-0007A-Stud bolt protrusion is less than 2 threads | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011988 |  | B | P | 18.2:Drg No TZ-MID-68-WPR2-206798, Item 06- Gate valve handle operation is stiff | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011989 |  | B | P | 18.3:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011990 |  | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011991 |  | B | P | 18.5:Paint touch up to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011992 |  | B | P | 18:Drg No TZ-MID-68-WPR2-206817, S14 (PS-51614) & TZ-MID-68-WPR2-206818 S4 (PS-58097) -GL01 gap shall be verified after PTFE pad installation | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011993 |  | B | P | 18.1:PS5-60-TG-0008A - Stud bolt protrusion is less than 2 threads | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011994 |  | B | P | 18.2:TZ-MID-68-WPR2-2067888, ITEM 06 - Gate valve handle operation is stiff | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011995 |  | B | P | 18.3:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-011996 |  | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-70 - Engine A Cooling system
PL-011997 |  | B | P | 18.5:Paint touch up to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-012137 | PS5_PNC_Install | C | I | PS005-PNC-COW - PS5-04-PNC-0001 ICSS Network Cabinet to be installed | Closed | 09-Aug-26 | PS5-83-01 - EITS Building
PL-012138 | PS5_PNC_NewCable | C | I | PS005-PNC-COW - PS5-04-PNC-0002 ICSS Network Cabinet to be installed | Closed | 2026-09-02 | PS5-83-01 - EITS Building
PL-012139 | PS5_INS | C | I | PS005-INS-COW - Cable TAG labels to be changed | Completed |  | PS5-83-01 - EITS Building
PL-012140 | PS5_ECS | C | E | PS005-ECS-COW - Cable TAG labels to be changed | Completed |  | PS5-83-01 - EITS Building
PL-012141 | PS5_ELE | C | E | PS005-ELE-COW - Cable TAG labels to be changed | Completed |  | PS5-83-01 - EITS Building
PL-012142 | PS5_TEL | C | T | PS005-TEL-COW - Cable TAG labels to be changed | Completed |  | PS5-83-01 - EITS Building
PL-012143 | PS5_HVAC | C | E | PS005-HVAC-COW - Cable TAG labels to be changed | Completed |  | PS5-83-01 - EITS Building
PL-012147 |  | B | P | 18:PS5-60-UR-8100C_TP1035 - Hose Connection FM to be Done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012148 |  | B | P | 18.1:Drg No TZ-MID-68-WPR2-207275, S13 (PS-64776) - PR01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-07 - Power Generation Package C
PL-012149 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-07 - Power Generation Package C
PL-012150 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012151 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012152 |  | B | P | 18.1:Drg No TZ-MID-68-WPR2-207266- Valve Handle Missing | Originated |  | PS5-60-07 - Power Generation Package C
PL-012153 |  | B | P | 18.2:PS5-60-UR-8100C_TP1034- Hose Connection FM to be Done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012154 |  | B | P | 18.3:Cladding Penetration to be Fixed | Originated |  | PS5-60-07 - Power Generation Package C
PL-012155 |  | B | P | 18.4:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-07 - Power Generation Package C
PL-012156 |  | B | P | 18.5:Paint touch up to be done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012157 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-10 - Power Generation Package D
PL-012158 |  | B | P | 18.1:TZ-MID-68-WPR2-207276 - Valve Handle Missing | Completed |  | PS5-60-10 - Power Generation Package D
PL-012159 |  | B | P | 18.2:PS5-60-UR-8100D_TP1036 & TP1037 - Hose Connection FM to be Done | Originated |  | PS5-60-10 - Power Generation Package D
PL-012160 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-10 - Power Generation Package D
PL-012161 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-10 - Power Generation Package D
PL-012162 | PS5-03-GDHS-E202-CW01 | B | I | Wrong tag number and not found at IO List | Originated |  | PS5-03-23 - FZ-E1 to E3 - EITS Building
PL-012163 | PS5-03-GDHS-E201-CW01 | B | I | Wrong tag number as per IO List | Originated |  | PS5-03-23 - FZ-E1 to E3 - EITS Building
PL-012164 |  | B | P | 18:PS5-60-UR-8100D_TP1039 - Hose Connection FM to be Done | Originated |  | PS5-60-10 - Power Generation Package D
PL-012165 |  | B | P | 18.1:Cladding Penetration to be Fixed | Completed |  | PS5-60-10 - Power Generation Package D
PL-012166 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-10 - Power Generation Package D
PL-012167 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-10 - Power Generation Package D
PL-012168 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-10 - Power Generation Package D
PL-012169 |  | B | P | 18.1:PS5-60-UR-8100D_TP1038 - Hose Connection FM to be Done | Originated |  | PS5-60-10 - Power Generation Package D
PL-012170 |  | B | P | 18.2:Cladding Penetration to be Fixed | Completed |  | PS5-60-10 - Power Generation Package D
PL-012171 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-10 - Power Generation Package D
PL-012172 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-10 - Power Generation Package D
PL-012207 | PS5-63-IEB-0001 | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 22 cables were verified on site | Originated |  | PS5-63-04 - Electrical Earthing - EITS Building
PL-012222 | PS5-63-IEB-0002 | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 27 cables were verified on site | Originated |  | PS5-63-04 - Electrical Earthing - EITS Building
PL-012223 | PS5-63-IEB-0003 | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 04 cables were verified on site. | Originated |  | PS5-63-04 - Electrical Earthing - EITS Building
PL-012224 | PS5-63-IEB-0004 | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 38 cables were verified on site. | Originated |  | PS5-63-04 - Electrical Earthing - EITS Building
PL-012225 | PS5-63-IEB-0005 | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 29 cables were verified on site. | Originated |  | PS5-63-04 - Electrical Earthing - EITS Building
PL-012226 | PS5-63-IEB-0006 | B | E | The cable quantity shown in Drawing No. TZ-MID-68-SSF1-150005 does not match the site installation. A total of 32 cables were verified on site. | Originated |  | PS5-63-04 - Electrical Earthing - EITS Building
PL-012237 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-06 - Crude Fuel Separation Module
PL-012238 |  | B | P | 18.1:PS5-71-SPZQ-0070 Tubing Connection FM to be Done | Originated |  | PS5-71-06 - Crude Fuel Separation Module
PL-012239 |  | B | P | 18.2:Cladding Penetration to be Fixed | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-012240 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-012241 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-012243 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-012244 |  | B | P | 18.1:Through Wall Penetration to be Fixed | Completed |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-012246 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-012250 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-18 - Diesel Separator Module
PL-012251 |  | B | P | 18.1:Cladding Penetration to be Fixed | Completed |  | PS5-71-18 - Diesel Separator Module
PL-012252 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-18 - Diesel Separator Module
PL-012253 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-71-18 - Diesel Separator Module
PL-012254 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-012255 |  | B | P | 18.1:PS5-71-PGD-0049A & PS5-71-PGD-0049B - to be install & FM to be done | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-012256 |  | B | P | 18.2:TZ-MID-68-WPR2-208033 Drawing RLMU To be done | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-012257 |  | B | P | 18.3:TZ-MID-68-WPR2-208033 Blank to ne Installed | Completed |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-012258 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-012369 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-012371 |  | B | P | 18.1:TZ-MID-68-WPR2-208365 CTR commodity code to be add & Valve Orientation RLMU to be done | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-012372 |  | B | P | 18.2:PS5-60-UR-8100D_TP852 & TP853 - Hose Connection FM to be Done | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-012373 | PS5-60-BE-0011A-CL01 | C | E | Cable Tagging not yet install at both ends | Originated |  | PS5-60-01 - Power Generation Package A
PL-012374 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-012375 | BF_PS5-61-IG-0003_CKT05 | B | E | DRAWING TO BE UPDATE AS PER SITE INSTALLATION | Originated |  | PS5-62-13 - EITS 33kV Bld. Normal L&SP DP - PS5-61-IG-0003
PL-012376 | PS5-60-BE-0011A-CL02 | C | E | Cable Tagging not yet install at both ends | Originated |  | PS5-60-01 - Power Generation Package A
PL-012377 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-012378 | PS5-60-BE-0011A-CL03 | C | E | Cable Tagging not yet install at both ends | Completed |  | PS5-60-01 - Power Generation Package A
PL-012379 | PS5-60-BE-0011B-CL01 | C | E | Cable Tagging not yet install at both ends | Completed |  | PS5-60-01 - Power Generation Package A
PL-012381 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-18 - Diesel Separator Module
PL-012382 | PS5-60-BE-0011B-CL03 | C | E | Cable Tagging not yet install at both ends | Completed |  | PS5-60-01 - Power Generation Package A
PL-012383 |  | B | P | 18.1:Sample Connection Inlet Connection FM to be Done | Originated |  | PS5-71-18 - Diesel Separator Module
PL-012384 | PS5-60-BE-0011B-CL05 | C | E | Cable Tagging not yet install at both ends | Completed |  | PS5-60-01 - Power Generation Package A
PL-012385 |  | B | P | 18.2:Drg No - TZ-MID-68-WPR2-207627, S12(PS-98188) - GL01 Missing | Completed |  | PS5-71-18 - Diesel Separator Module
PL-012386 |  | B | P | 18.3:Drg No- TZ-MID-68-WPR2-207627, S12 & S13 (PS-49018)- GL01 & PR01 Missing Structure support not Installed | Originated |  | PS5-71-18 - Diesel Separator Module
PL-012389 |  | B | P | 18.4:TZ-MID-68-WPR2-207469, F2 - Flange Management to be done | Originated |  | PS5-71-18 - Diesel Separator Module
PL-012390 | PS5-60-BE-0012A-CL03 | C | E | Cable Tagging not yet install at both ends | Completed |  | PS5-60-04 - Power Generation Package B
PL-012391 |  | B | P | 18.5:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-18 - Diesel Separator Module
PL-012392 |  | B | P | 18.6:Paint touch up to be done | Completed |  | PS5-71-18 - Diesel Separator Module
PL-012393 | PS5-60-BE-0012A-CL05 | C | E | Cable tagging to be installed at both ends | Completed |  | PS5-60-04 - Power Generation Package B
PL-012396 |  | B | P | 18:1"Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012405 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-012408 |  | B | P | 18.1:Drg No- TZ-MID-68-WPR2-206863, S10 & S11 (51586 - PR01 & GL01 Not done bottom structure supports have not yet been installed. | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-012410 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-012411 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-012427 | PS5-60-TG-0007A | C | I | Cable Tagging not yet install at both ends | Originated |  | PS5-60-70 - Engine A Cooling system
PL-012430 | PS5-60-TG-0008A | C | I | Cable Tagging not yet install at both ends | Originated |  | PS5-60-70 - Engine A Cooling system
PL-012433 | PS5-60-TG-0006A | C | I | Cable Tagging not yet install at both ends | Originated |  | PS5-60-70 - Engine A Cooling system
PL-012434 | PS5-60-TG-0006B | C | I | Cable Tagging not yet install at both ends | Originated |  | PS5-60-71 - Engine B Cooling system
PL-012435 | PS5-60-TG-0005A | C | I | Cable Tagging not yet install at both ends | Originated |  | PS5-60-70 - Engine A Cooling system
PL-012436 | PS5-60-TG-0005B | C | I | Cable Tagging not yet install at both ends | Originated |  | PS5-60-71 - Engine B Cooling system
PL-012467 | PS5-61-IK-0001-CL01 | C | E | Missing cable tag - Inside Panel & Cabin (Yellow tag with black font) | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012469 | PS5-61-IK-0001-CL01 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012471 | PS5-61-IJ-0010-CL01 | C | E | Missing Indoor & Inside Cabin Yellow Colour Black Font Cable Tag | Originated |  | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010)
PL-012472 | PS5-61-IJ-0010-CL01 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010)
PL-012473 | PS5-61-IK-0001-CL03 | C | E | Missing cable tag - Indoor & Inside cabin (Yellow tag with black font) | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012474 | PS5-61-IK-0001-CL03 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012475 |  | B | P | 18:Gladding Penetration to be fixed | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-012476 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-012477 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-71-06 - Crude Fuel Separation Module
PL-012478 |  | B | P | 18:Drg No -TZ-MID-68-WPR2-208146, S13 (PS86704)- PR01 to be fixed | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012479 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012480 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012481 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012484 |  | B | P | 18:Gladding Penetration to be fixed | Completed |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-012485 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-012486 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-012487 | PS5-61-IK-0001-CL04 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012488 | PS5-61-IK-0001-CL04 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012489 | PS5-61-IK-0001-CL05 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012490 | PS5-61-IK-0001-CL05 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012491 | PS5-61-IK-0001-CL06 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012492 | PS5-61-IK-0001-CL06 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012493 | PS5-61-IK-0001-CL07 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012494 | PS5-61-IK-0001-CL07 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012495 | PS5-61-IK-0001-CL08 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012496 | PS5-61-IK-0001-CL08 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012497 | PS5-61-IK-0001-CL09 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012498 | PS5-61-IK-0001-CL09 | B | E | Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012499 | PS5-61-IK-0001-CL10 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012500 | PS5-61-IK-0001-CL10 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012501 | PS5-61-IK-0001-CL11 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012502 | PS5-61-IK-0001-CL11 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012503 | PS5-61-IK-0001-CL12 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012504 | PS5-61-IK-0001-CL12 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012505 | PS5-61-IK-0001-CL13 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012506 | PS5-61-IK-0001-CL13 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012507 | PS5-61-IK-0001-CL14 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012508 | PS5-61-IK-0001-CL14 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012509 | PS5-61-IK-0001-CL15 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012510 | PS5-61-IK-0001-CL15 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012511 | PS5-61-IK-0001-CL16 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012512 | PS5-61-IK-0001-CL16 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012513 | PS5-61-IK-0001-CL17 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012514 | PS5-61-IK-0001-CL17 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012515 | PS5-61-IK-0001-CL18 | C | E | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012516 | PS5-61-IK-0001-CL18 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-012690 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-012691 |  | B | P | 18.1:Through Wall Penetration to be Fixed. | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-012692 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-27 - Compressed Air Starting Skid
PL-012693 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-27 - Compressed Air Starting Skid
PL-012694 |  | B | P | 18:PS5-60-UR-8100D_TP-848 & TP-849- Hose connection joint FM to be done | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-012695 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-012696 |  | B | P | 18.2:Floor Penetration to be Fixed. | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-012697 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-38 - Injector Tip Cooling Module D
PL-012698 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-38 - Injector Tip Cooling Module D
PL-012699 |  | B | P | 18:PS5-60-UR-8100B_TP-812,TP-813 & TP-814-Hose connection joint FM to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-012700 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-71 - Engine B Cooling system
PL-012701 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-71 - Engine B Cooling system
PL-012703 | PS5-05-BI-0002-CC11 | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012704 | PS5-05-BI-0002-CC11 | B | I | No Proper Heat Sleeve for Screen | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012705 | PS5-05-BI-0002-CC11 | B | I | No Proper Earth Clamp | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012706 | PS5-05-BI-0002-CC11 | B | I | No Proper MCT Packing | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012707 | PS5-05-BI-0002-CC12 | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012708 | PS5-05-BI-0002-CC12 | B | I | No Proper Heat Sleeve for Screen | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012709 | PS5-05-BI-0002-CC12 | B | I | No Proper Earth Clamp for Armour Earth | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012710 | PS5-05-BI-0002-CC12 | B | I | No Proper pack the MCT | Originated |  | PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure
PL-012729 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012730 |  | B | P | 18.1:PS5-60-UR-8100C_TP-1032 & TP-1033 - Hose connection joint FM to be done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012731 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-07 - Power Generation Package C
PL-012732 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-60-07 - Power Generation Package C
PL-012733 |  | B | P | 18:PS5-60-UR-8100C_TP-828 & TP-827, PS5-60-UZ-8100C_TP-354 & TP-357 - connection joint FM to be done | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-012734 |  | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-012735 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-012736 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-012737 |  | B | P | 18:PS5-60-UR-8100C_TP-831 & TP-832- Hose connection joint FM to be done | Originated |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-012738 |  | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-012739 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-012740 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-012741 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-012742 |  | B | P | 18.1:Floor Penetration Gratings to be Fixed. | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-012743 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-012744 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-012745 |  | B | P | 18:PS5-60-UR-8100A_TP-791, TP-792 & TP-793 - Hose connection joint FM to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-012746 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-70 - Engine A Cooling system
PL-012747 |  | B | P | 18.2:Paint touch up to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-012768 | PS5-60-BI-0016A-CC02 | C | I | Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-01 - Power Generation Package A
PL-012769 | PS5-60-IE-0003A-CC02 | C | I | Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-012770 | PS5-60-IE-0003A-CC03 | C | I | Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-012771 | PS5-60-IE-0003A-CC04 | C | I | Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-012772 | PS5-60-IE-0003A-CC15 | C | I | Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-012783 |  | B | P | 18.1:Through Wall penetration to be Fixed | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012784 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012785 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-012828 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-28 - Air Receiver A & Air Regulator A
PL-012829 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-28 - Air Receiver A & Air Regulator A
PL-012831 |  | B | P | 18.2:Paint touch up to be done | Originated |  | PS5-60-28 - Air Receiver A & Air Regulator A
PL-012836 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-012838 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-012839 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-012844 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-012847 |  | B | P | 18:Paint touchup to be done | Completed |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-012851 |  | B | P | 18:PS5-60-UR-8100D_TP-854, TP-855 & TP-856 - Hose connection joint Flange management to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-012852 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-73 - Engine D Cooling system
PL-012853 |  | B | P | 18.2:Paint touch up to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-012884 | PS5-60-PG-0002A | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-28 - Air Receiver A & Air Regulator A
PL-012885 | PS5-60-PG-0002B | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-012928 | PS5-60-IH-0001A-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012937 | PS5-60-IH-0001A-CL01 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012941 | PS5-60-IH-0001A-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012942 | PS5-60-IH-0001A-CL02 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012945 | PS5-60-IH-0001A-CL03 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012947 | PS5-60-IH-0001A-CL03 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012950 | PS5-60-IH-0001A-CL04 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012952 | PS5-60-IH-0001A-CL04 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-012956 | PS5-60-IH-0001B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-012957 | PS5-60-IH-0001B-CL01 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-012963 | PS5-60-IH-0001B-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-012965 | PS5-60-IH-0001B-CL02 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-012966 | PS5-60-IH-0001B-CL03 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-012967 | PS5-60-IH-0001B-CL03 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-012970 | PS5-60-IH-0001B-CL04 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-012971 | PS5-60-IH-0001B-CL04 | C | E | Core marking to be installed at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-013023 |  | B | P | 18:Paint touch up to be done | Originated |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-013024 |  | B | P | 18:PS5-60-UR-8100C_TP-825 7 TP_826 - Equpiment connection joint Flange Management to be done | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-013025 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-013026 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-013027 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-013029 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-013030 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-013031 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-013053 | PS5-60-TX-41300A | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-72 - Engine C Cooling system
PL-013056 | PS5-60-TX-41300A | C | E | 23.1:EARHING TO BE DONE | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013058 | PS5-60-TX-41300B | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-72 - Engine C Cooling system
PL-013063 | PS5-60-TX-41300B | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013065 | PS5-60-TX-41300B | C | E | 23.2: EARTHING TO BE DONE | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013067 | PS5-60-TX-41300A | C | M | 23.2:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013068 | PS5-60-TX-41400A | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-73 - Engine D Cooling system
PL-013070 | PS5-60-TX-41400A | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-73 - Engine D Cooling system
PL-013071 | PS5-60-TX-41400A | C | E | 23.2: EARTHING TO BE DONE | Originated |  | PS5-60-73 - Engine D Cooling system
PL-013077 | PS5-60-TX-41400B | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-60-73 - Engine D Cooling system
PL-013078 | PS5-60-TX-41400B | C | M | 23.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-60-73 - Engine D Cooling system
PL-013079 | PS5-60-TX-41400B | C | E | 23.2:EARTHING TO BE DONE | Originated |  | PS5-60-73 - Engine D Cooling system
PL-013084 | PS5-71-VSV-1200 | B | P | 18:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-013086 | PS5-71-VSV-1200 | C | M | 18.1:Touch up / painting to be completed wherever required on the equipment | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-013088 | PS5-71-VSV-1200 | C | E | 18.2:EARTHING TO BE DONE | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-013120 | PS5-71-VSV-1200 | B | P | 11:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-20 - Diesel Fuel Day Tank
PL-013124 | PS5-71-VSV-1200 | C | M | 11.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-013125 | PS5-71-VSV-1200 | C | E | 11.2:EARTHING TO BE DONE | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-013252 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-013253 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-013254 |  | B | P | 18.2:Paint touch up to be done | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-013256 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-013257 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-013258 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-013260 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-013261 |  | B | P | 18.1:PS5-60-UR-8100D-TP_846 & 847 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-013262 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-013263 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-013448 | PS5-60-IE-0003A-CD02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013451 | PS5-60-IE-0003A-CD03 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013455 | PS5-60-IE-0003A-CD05 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013461 | PS5-60-IE-0003A-CD08 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013466 | PS5-60-IE-0003A-CD12 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013471 | PS5-60-IE-0003A-CD14 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013476 | PS5-71-DM-3500A-CL01 | B | E | Earthing stud of motor not connected to earthing boss at field side | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013478 | PS5-71-DM-3500B-CL01 | B | E | Earthing stud of motor not connected to earthing boss at field side | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013514 | PS5-60-PG-0002C | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-013516 | PS5-60-PG-0002D | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-013517 | PS5-60-TG-0005C | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013518 | PS5-60-TG-0006C | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013519 | PS5-60-TG-0007C | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013521 | PS5-60-TG-0008C | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013608 | PS5-71-SPZQ-0067 | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013609 | PS5-71-SPZQ-0067 | C | M | 8.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013610 | PS5-71-SPZQ-0066 | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-71-18 - Diesel Separator Module
PL-013611 | PS5-71-SPZQ-0066 | C | M | 8.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-71-18 - Diesel Separator Module
PL-013614 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-23 - Instrument Air Distribution lines
PL-013615 |  | B | P | 18.1:TZ-MID-68-WPR2-207161,TZ-MID-68-WPR2-207162,TZ-MID-68-WPR2-207166,TZ-MID-68-WPR2-208131 & TZ-MID-68-WPR2-20802 - ISO RLMU to be done | Originated |  | PS5-60-23 - Instrument Air Distribution lines
PL-013616 |  | B | P | 18.2:Equpiment connection joint Flange Management to be done | Originated |  | PS5-60-23 - Instrument Air Distribution lines
PL-013617 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-23 - Instrument Air Distribution lines
PL-013618 |  | B | P | 18.4:Paint touch up to be done | Completed |  | PS5-60-23 - Instrument Air Distribution lines
PL-013619 |  | B | P | 18:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013620 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013621 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013622 |  | A | P | 18.3:Iten 04, TZ-MID-68-WPR2-206788 - Orifice Flange 1/2" Nipple & Flange to be install | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013623 |  | A | P | 18.4:ITEM 01, 02 & 03-(TZ-MID-68-WPR2-206883 & TZ-MID-68-WPR2-206883) - PS5-71-FIT-0019 _01 & 02 to be installed. | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013624 |  | A | P | 18.5:PS5 71 PG-0050A & PS5 71 PG-0050B - PRESSURE INSTRUMENT to be install & Flange Management to be done | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-013625 |  | B | P | 18:Paint touch up to be done | Originated |  | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E
PL-013626 |  | B | P | 18:PS5-60-UR-8100C-TP_833, TP_834 & TP_835 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013627 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013628 |  | B | P | 18.2:Paint touch up to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-013636 | PS5-05-IE-8100-CC01 | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013637 | PS5-05-IE-8100-CC01 | B | I | MCT not Properly Closed | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013638 | PS5-05-IE-8100-CC01 | B | I | No Proper Armour Earth | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013639 | PS5-05-IE-8100-CC01 | B | I | No Proper Cable Dressing inside the Panel | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013640 | PS5-05-IE-8100-CC02 | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013641 | PS5-05-IE-8100-CC02 | B | I | No Proper Armour Earthing | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013642 | PS5-05-IE-8100-CC02 | B | I | No Properly closed the MCT Entry | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013643 | PS5-05-IE-8100-CC02 | C | I | No Cable Tag (Outdoor Metal Tag) | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013645 | PS5-05-IE-8100-CD09 | C | E | Missing Indoor Cable Tag (Yellow Colour With Black Font) | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013646 | PS5-05-IE-8100-CD22 | C | E | Missing Indoor Cable Tag (Yellow Colour With Black Font) | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013647 | PS5-05-IE-8100-CD24 | C | E | Missing Indoor Cable Tag (Yellow Colour With Black Font) | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-013648 | PS5-61-IK-0001-CL02 | B | E | Not Used the proper Nut Bolts for Transformer Side Termination points | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-013649 | PS5-61-IK-0001-CL02 | C | E | Missing cable tag - Indoor & Inside cabin (Yellow tag with black font) | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-013655 | PS5-60-TG-0006E | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-74 - Engine E Cooling system
PL-013657 | PS5-60-TG-0007E | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-74 - Engine E Cooling system
PL-013659 | PS5-60-TG-0008E | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-74 - Engine E Cooling system
PL-013681 |  | B | P | 18: 1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-13 - Power Generation Package E
PL-013682 |  | B | P | 18.1:PS5-60-UR-8100E-TP_1040 & TP_1041 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-13 - Power Generation Package E
PL-013683 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-13 - Power Generation Package E
PL-013684 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-13 - Power Generation Package E
PL-013685 | PS5-60-BE-0025A-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-013687 | PS5-60-BE-0025B-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-013688 | PS5-60-BE-0026A-CL02 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-70 - Engine A Cooling system
PL-013689 | PS5-60-BE-0026B-CL02 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-71 - Engine B Cooling system
PL-013690 | PS5-60-BI-0015A-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-01 - Power Generation Package A
PL-013691 | PS5-60-BI-0015A-CL01 | B | E | Mismatching Drawing at Skid Side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013692 | PS5-60-BI-0015A-CL02 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-01 - Power Generation Package A
PL-013693 | PS5-60-BI-0015A-CL02 | B | E | Mismatching Drawing at Skid Side | Originated |  | PS5-60-01 - Power Generation Package A
PL-013694 | PS5-60-BI-0015B-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-04 - Power Generation Package B
PL-013695 | PS5-60-BI-0015B-CL01 | B | E | Mismatching Drawing at Skid Side | Originated |  | PS5-60-04 - Power Generation Package B
PL-013696 | PS5-60-BI-0015B-CL02 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-04 - Power Generation Package B
PL-013697 | PS5-60-BI-0015B-CL02 | B | E | Mismatching Drawing at Skid Side | Originated |  | PS5-60-04 - Power Generation Package B
PL-013698 | PS5-60-BI-0015B-CL03 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-04 - Power Generation Package B
PL-013699 | PS5-60-BI-0015B-CL03 | B | E | Mismatching Drawing at Skid Side | Originated |  | PS5-60-04 - Power Generation Package B
PL-013700 | PS5-60-IN-0001A-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-013701 | PS5-60-IN-0001B-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-013702 | PS5-60-VS-9100A-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-013703 | PS5-60-VS-9100B-CL01 | B | E | Earthing Cable for Earthing tag not yet installed at both end Glands | Originated |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-013704 |  | B | P | 18:PS5-60-UR-8100E-TP_1043 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-13 - Power Generation Package E
PL-013705 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-13 - Power Generation Package E
PL-013706 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-13 - Power Generation Package E
PL-013708 |  | B | P | 18:PS5-60-UR-8100E-TP_0873 & TP_0874 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E
PL-013709 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E
PL-013710 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E
PL-013711 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E
PL-013712 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-013713 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-013714 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-013715 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-013716 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-013717 |  | B | P | 18.2:Paint touch up to be done | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-013719 | PS5-28-PA-3300 | B | M | 14:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-013720 | PS5-28-PA-3300 | C | M | 14.1:TOUCH UP/PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-013721 | PS5-28-PA-3300 | C | M | 14.2:EARTHING TO BE DONE | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-013722 | PS5-75-UI-6100 | B | P | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-75-02 - Biocide Injection Package
PL-013723 | PS5-75-UI-6100 | C | M | 10.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-75-02 - Biocide Injection Package
PL-013764 | PS5-60-01_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-01 - Power Generation Package A
PL-013821 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-35 - Injector Tip Cooling Module A
PL-013822 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-60-35 - Injector Tip Cooling Module A
PL-013828 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-36 - Injector Tip Cooling Module B
PL-013829 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-60-36 - Injector Tip Cooling Module B
PL-013831 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-013832 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-013833 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-013834 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-013836 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-013838 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-013859 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-013860 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-013909 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-13 - Power Generation Package E
PL-013910 |  | B | P | 18.1:PS5-60-UR-8100E_TP-1042 - Equpiment Hose connection Flange Management to be done | Originated |  | PS5-60-13 - Power Generation Package E
PL-013911 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-13 - Power Generation Package E
PL-013913 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-13 - Power Generation Package E
PL-013922 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-16 - Power Generation Package F
PL-013923 |  | C | P | 18.1:PS5-60-UR-8100F_TP-1044 & TP-1045 - Equpiment Hose connection Flange Management to be done | Originated |  | PS5-60-16 - Power Generation Package F
PL-013924 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-16 - Power Generation Package F
PL-013925 |  | B | P | 18.3:Paint touchup to be done | Completed |  | PS5-60-16 - Power Generation Package F
PL-013926 |  | B | P | 18:PS5-60-UR-8100F_TP-1047 - Equpiment Hose connection Flange Management to be done | Originated |  | PS5-60-16 - Power Generation Package F
PL-013927 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-16 - Power Generation Package F
PL-013928 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-16 - Power Generation Package F
PL-013931 | PS5-60-BE-0001-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-013932 | PS5-60-BE-0001-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-013933 | PS5-60-BE-0001-CL04 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-013935 | PS5-60-BE-0002-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-013936 | PS5-60-BE-0002-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-013939 | PS5-60-BE-0002-CL03 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-013943 | PS5-60-IH-0002-CL07 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013944 | PS5-60-IH-0002-CL07 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013945 | PS5-60-IH-0002-CL08 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013947 | PS5-60-IH-0002-CL08 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013948 | PS5-60-IH-0002-CL09 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013949 | PS5-60-IH-0002-CL09 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013952 | PS5-60-IH-0002-CL10 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013954 | PS5-60-IH-0002-CL10 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-013958 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-16 - Power Generation Package F
PL-013960 |  | B | P | 18.1:PS5-60-UR-8100F_TP-1046 - Equpiment Hose connection Flange Management to be done | Originated |  | PS5-60-16 - Power Generation Package F
PL-013961 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-16 - Power Generation Package F
PL-013962 |  | B | P | 18.3:Paint touchup to be done | Completed |  | PS5-60-16 - Power Generation Package F
PL-013964 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F
PL-013965 |  | B | P | 18.1:PS5-60-UR-8100F_TP-894 & TP_895 - Equpiment Hose connection Flange Management to be done | Originated |  | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F
PL-013966 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F
PL-013968 |  | B | P | 18.3:Paint touch up to be done | Completed |  | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F
PL-013973 |  | B | P | 18:PS5-60-UR-8100E_TP-867 & TP-868 - Equpiment connection Flange Management to be done | Originated |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-013974 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-013975 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-013976 |  | B | P | 18.3:Paint touchup to be done | Completed |  | PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E
PL-014011 | PS5-61-IK-0001-CL38 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014012 | PS5-61-IK-0001-CL38 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014016 | PS5-61-IK-0001-CL39 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014017 | PS5-61-IK-0001-CL39 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014019 | PS5-61-IK-0001-CL40 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014020 | PS5-61-IK-0001-CL40 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014021 | PS5-01-UB-6100_PIPING_OUTSIDE_BUILDING | B | P | The flange connection is resting directly on top of the pipe support. Normally, flange connections should remain free from any obstruction to allow access for future maintenance and flange opening activities. | Originated |  | PS5-01-09 - Inergen for EITS Building
PL-014022 | PS5-61-IK-0001-CL41 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014023 | PS5-61-IK-0001-CL41 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014029 | PS5-61-IK-0001-CL42 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014032 | PS5-61-IK-0001-CL42 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014039 | PS5-61-IK-0001-CL43 | B | E | INSULATION TESTER KEW 3125A W8501159 | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014040 | PS5-61-IK-0001-CL43 | C | E | Permanent Core marking to be installed at both side | Originated |  | PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001)
PL-014053 | PS5-60-TG-0005F | B | I | Permanent tags and hanging tags to be installeds | Originated |  | PS5-60-75 - Engine F Cooling system
PL-014058 | PS5-60-TG-0006F | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-75 - Engine F Cooling system
PL-014060 | PS5-60-TG-0007F | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-75 - Engine F Cooling system
PL-014061 | PS5-60-TG-0008F | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-75 - Engine F Cooling system
PL-014087 | PS5-60-IE-0003A-CC01 | B | I | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014088 | PS5-60-IE-0003A-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014091 | PS5-60-IE-0003A-CC06 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014092 | PS5-60-IE-0003A-CC07 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014093 | PS5-60-IE-0003A-CC08 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014094 | PS5-60-IE-0003A-CC05 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014112 | PS5-60-BE-0007B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014113 | PS5-60-BE-0007B-CL01 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014115 | PS5-60-BE-0007B-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014116 | PS5-60-BE-0007B-CL02 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014118 | PS5-60-BE-0007B-CL03 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014119 | PS5-60-BE-0007B-CL03 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014120 | PS5-60-BI-0006A-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014121 | PS5-60-BI-0006A-CL01 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014122 | PS5-60-BI-0006A-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014125 | PS5-60-BI-0006A-CL03 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014126 | PS5-60-BI-0006A-CL03 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014128 | PS5-60-BI-0006A-CL04 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014129 | PS5-60-BI-0006A-CL04 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014131 | PS5-60-BI-0006A-CL05 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014132 | PS5-60-BI-0006A-CL05 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014134 |  | A | P | 18:Collection Pot Connection & Installation to be done | Originated |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-014135 | PS5-60-BI-0006A-CL06 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014136 | PS5-60-BI-0006A-CL06 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014137 |  | B | P | 18.1:Paint touch up to be done | Originated |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-014138 | PS5-60-BI-0006A-CL07 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014139 | PS5-60-BI-0006A-CL07 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014140 | PS5-60-BI-0006A-CL08 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014141 | PS5-60-BI-0006A-CL08 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014142 |  | A | P | 18:Collection Pot Connection & Installation to be done | Originated |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-014143 | PS5-60-BI-0006A-CL09 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014144 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-014145 | PS5-60-BI-0006A-CL09 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014146 | PS5-60-BI-0006A-CL10 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014148 | PS5-60-BI-0006A-CL10 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014150 | PS5-60-BI-0006A-CL11 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014151 | PS5-60-BI-0006A-CL11 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014152 | PS5-60-BI-0006B-CL04 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014153 | PS5-60-BI-0006B-CL04 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014154 | PS5-60-BI-0006B-CL05 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014155 | PS5-60-BI-0006B-CL05 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014157 | PS5-60-BI-0006B-CL06 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014158 | PS5-60-BI-0006B-CL06 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014159 | PS5-60-BI-0006B-CL10 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014160 | PS5-60-BI-0006B-CL10 | C | E | SS Cables Tags not yet Install BOTH SIDE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014199 |  | B | P | 18:Paint touch up to be done | Originated |  | PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G
PL-014202 |  | B | P | 18:PS5-60-UR-8100G-TP_1048 & TP_1049 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-19 - Power Generation Package G
PL-014203 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-19 - Power Generation Package G
PL-014204 |  | B | P | 18.2:Paint touchup to be done | Originated |  | PS5-60-19 - Power Generation Package G
PL-014213 |  | B | P | 18:PS5-60-UR-8100G-TP_1051 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-19 - Power Generation Package G
PL-014214 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-60-19 - Power Generation Package G
PL-014215 |  | B | P | 18.2:Paint touchup to be done | Originated |  | PS5-60-19 - Power Generation Package G
PL-014217 |  | B | P | 18:PS5-60-UR-8100G-TP_1050 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-19 - Power Generation Package G
PL-014218 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-19 - Power Generation Package G
PL-014220 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-19 - Power Generation Package G
PL-014221 |  | B | P | 18.3:Paint touchup to be done | Originated |  | PS5-60-19 - Power Generation Package G
PL-014235 |  | B | P | 18:ITEM 14 / PS5-60-PG-0002G - Instrument joint Flange Management to be done | Originated |  | PS5-60-34 - Air Receiver G & Air Regulator G
PL-014236 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-34 - Air Receiver G & Air Regulator G
PL-014237 |  | B | P | 18.2:Paint touch up to be done | Originated |  | PS5-60-34 - Air Receiver G & Air Regulator G
PL-014239 |  | B | P | 18:PS5-60-UR-8100E_TP-875,TP-876 & TP-877 - Equpiment joint Flange Management to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-014240 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-74 - Engine E Cooling system
PL-014241 |  | B | P | 18.2:Paint touch up to be done | Completed |  | PS5-60-74 - Engine E Cooling system
PL-014269 | PS5-60-BI-0006A-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014272 | PS5-60-BI-0006A-CC02 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP)
PL-014273 | PS5-60-BI-0006A-CC03 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP)
PL-014274 | PS5-60-BI-0006A-CC04 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP)
PL-014276 | PS5-60-BI-0006A-CC05 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP)
PL-014277 | PS5-60-BI-0006A-CC06 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP)
PL-014278 | PS5-60-BI-0017A-CC02 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-014279 | PS5-60-VS-9101A-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-014280 | PS5-60-VS-9101B-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-014286 | PS5-05-IE-8100-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-014287 | PS5-05-IE-8100-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-014288 | PS5-60-BI-0005A-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-01 - Power Generation Package A
PL-014289 | PS5-60-BI-0005B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-04 - Power Generation Package B
PL-014290 | PS5-60-IE-0002B-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-04 - Power Generation Package B
PL-014291 | PS5-60-IE-0003A-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014292 | PS5-60-IE-0003A-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014293 | PS5-60-IE-0003B-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-014294 | PS5-60-IH-0001A-CL06 | A | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Completed |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-014295 | PS5-60-IH-0001B-CL06 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-014303 | PS5-05-IE-8100-CD09 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-014304 | PS5-05-IE-8100-CD22 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-014305 | PS5-05-IE-8100-CD24 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-05-02 - Emergency Diesel Generator Package (UCP)
PL-014306 | PS5-60-BE-0024A-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-014307 | PS5-60-BE-0024A-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-014308 | PS5-60-BE-0024B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-014309 | PS5-60-BE-0024B-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-014311 | PS5-60-BI-0001A-CC01 |  | I | 14: | Originated |  | PS5-60-01 - Power Generation Package A
PL-014314 | PS5-60-IE-0003A-CC09 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014318 | PS5-60-IE-0003A-CC17 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014319 | PS5-60-IE-0003A-CC23 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014320 | PS5-60-IE-0003A-CC24 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014399 | PS5-75-UI-6300 | B | M | 4:The nut for the 1/2-inch pipe U-clamp was missing. | Originated |  | PS5-75-03 - Corrosion Inhibitor Injection Package
PL-014400 | PS5-75-UI-6300 | B | M | 4.1:The U-clamp was found to be improperly installed | Originated |  | PS5-75-03 - Corrosion Inhibitor Injection Package
PL-014401 | PS5-75-UI-6300 | A | M | 4.2:"Oil leakage was observed from the diaphragm pump (PS5-75-PB-3100A)." | Originated |  | PS5-75-03 - Corrosion Inhibitor Injection Package
PL-014402 | PS5-75-UI-6300 | A | M | 4.3:"Oil leakage was observed from the diaphragm pump (PS5-75-PB-3100B)." | Originated |  | PS5-75-03 - Corrosion Inhibitor Injection Package
PL-014403 | PS5-75-UI-6300 | B | M | 4.4:The vent holes on the pad plate are not sealed | Originated |  | PS5-75-03 - Corrosion Inhibitor Injection Package
PL-014404 | PS5-75-UI-6300 | B | M | 4.5: 2" pipe U-clamp was found missing | Originated |  | PS5-75-03 - Corrosion Inhibitor Injection Package
PL-014405 | PS5-75-UI-6300 | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Completed |  | PS5-75-03 - Corrosion Inhibitor Injection Package
PL-014421 | PS5-25-PA-3100A | B | M | "The material with Serial No. 104490004028 arrived without a packing list and is an overage item (Attach picture)" | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-014423 | PS5-25-PA-3100A | B | M | "The material with Serial No. 104490004028 arrived without a packing list and is an overage item (Attach picture)" | Completed |  | PS5-25-02 - Crude Oil Export Pump A
PL-014430 | PS5-25-PA-3100A | B | M | "The material with Serial No. 104490004028 arrived without a packing list and is an overage item (Attach picture)" | Completed |  | PS5-25-02 - Crude Oil Export Pump A
PL-014433 | PS5-74-UB-5100 | A | M | The spool is not suitable for installation. The spool needs to be modified to fit properly and allow correct installation. | Completed |  | PS5-74-01 - N2 Generation Skid
PL-014444 | PS5-71-IN-0003-CC06 | C | I | Missing Indoor Cable Tag(Yellow Tag) | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014445 | PS5-71-IN-0003-CC06 | B | I | No Proper MCT Packing | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014446 | PS5-71-IN-0003-CC06 | B | I | No Proper Earth clamp for Armour | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014447 | PS5-71-IN-0003-CC06 | C | I | Missing Metal cable tag | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014458 | PS5-71-IN-0003-CC07 | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014459 | PS5-71-IN-0003-CC07 | B | I | No Proper Earth Clamp for Armour Earth | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014460 | PS5-71-IN-0003-CC07 | B | I | The MCT is not closed properly. | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014461 | PS5-71-IN-0003-CC07 | C | I | Missing Metal Cable Tag (Out Door) | Completed |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-014462 | PS5-25-BI-1301-CC01 | C | I | Missing Indoor Cable Tag (Yellow Colour With Black Font) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014463 | PS5-25-BI-2301-CC01 | C | I | Missing Indoor Cable Tag (Yellow Colour With Black Font) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014464 | PS5-25-BI-2301-CC01 | C | I | Missing Metal Cable Tag (Out Door) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014465 | PS5-25-BI-2312-CC01 | C | I | Missing Indoor Cable Tag (Yellow Colour With Black Font) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014466 | PS5-25-BI-2312-CC01 | B | I | No Proper Earth Clamp for Armour Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014467 | PS5-25-BI-2312-CC01 | C | I | Missing the Metal Cable Tag (Outdoor) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014468 | PS5-60-IE-0003A-CC21 | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014469 | PS5-60-IE-0003A-CC21 | B | I | No Proper Earth Clamp for Armour Earth | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014470 | PS5-60-IE-0003A-CC21 | B | I | MCT not Properly Closed | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014484 | PS5-61-IU-0001A |  | E | 22: | Originated |  | PS5-60-01 - Power Generation Package A
PL-014504 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-014505 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-014506 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-71-01 - CFO Storage Tank Feed Heater
PL-014507 |  | B | P | 18:Pickling and passivation to be done | Originated |  | PS5-01-02 - Fire Water Pump A
PL-014508 |  | B | P | 18.1:Pickling and passivation to be done | Originated |  | PS5-01-02 - Fire Water Pump A
PL-014509 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-014514 |  | B | P | 18:Pickling and passivation | Originated |  | PS5-71-15 - Diesel Fuel Storage Tank
PL-014541 | PS5-25-BI-2305-CC01 | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014542 | PS5-25-BI-2305-CC01 | B | I | No Proper Earth Clamp for Armour Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014543 | PS5-60-IE-0003B-CC21 | C | I | Missing Indoor Cable Tag (Yellow Colour with Black font) | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-014544 | PS5-60-IE-0003B-CC21 | B | I | MCT not Properly Closed | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-014545 | PS5-60-IE-0003B-CC21 | B | I | No Proper Earth clamp for Armour | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-014546 | PS5-60-IE-0003B-CC21 | C | I | Missing Outdoor Metal Cable Tag | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-014552 | PS5-71-BI-1305-CC01 | C | I | Missing Cable Tag-Indoor/Inside Cabin Yellow Colour tag with Black Font | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014553 | PS5-71-BI-1305-CC01 | B | I | No Proper Earth clamp for Armour | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014554 | PS5-71-BI-1305-CC01 | C | I | Missing Outdoor Metal Cable Tag | Originated |  | PS5-91-01 - Multicore cables & JB
PL-014555 | PS5-71-BI-2317-CC01 | C | I | Missing Indoor Cable tag (Yellow tag With Black Font) | Originated |  | PS5-71-15 - Diesel Fuel Storage Tank
PL-014556 | PS5-71-BI-2317-CC01 | B | I | No Proper Earth Clamp for Armour Earth | Originated |  | PS5-71-15 - Diesel Fuel Storage Tank
PL-014557 | PS5-71-BI-2317-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-71-15 - Diesel Fuel Storage Tank
PL-014558 | PS5-71-BI-2317-CC01 | C | I | Missing Outdoor Metal Cable Tag | Originated |  | PS5-71-15 - Diesel Fuel Storage Tank
PL-014590 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014591 |  | B | P | 18.1:PS5-60-UR-8100C_TP-821 & TP-823 - Equpiment joint Flange Management up to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014592 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014593 |  | B | P | 18.3:Paint touchup to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014594 |  | B | P | 18:PS5-60-UR-8100C_TP-824 - Equpiment joint Flange Management up to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014595 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014596 |  | B | P | 18.2:TZ-MID-68-WPR2-207120 & TZ-MID-68-WPR2-207123 - Trunnion support to be welded to Structure | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014597 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014598 |  | B | P | 18.4:Paint touch up to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014601 |  | B | P | 18:PS5-60-UR-8100C_TP-822 - Equpiment joint Flange Management up to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014602 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014603 |  | B | P | 18.2:TZ-MID-68-WPR2-207128 & TZ-MID-68-WPR2-207131 - Trunnion to be welded to Structure | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014604 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014605 |  | B | P | 18.4:Paint touchup to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014608 |  | B | P | 18:1" V alve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014609 |  | B | P | 18.1:TZ-MID-68-WPR2-207133 & TZ-MID-68-WPR2-207137 - Trunnion to be welded to Structure | Completed |  | PS5-60-72 - Engine C Cooling system
PL-014610 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-72 - Engine C Cooling system
PL-014611 |  | B | P | 18.3:Paint touchup to be done | Completed |  | PS5-60-72 - Engine C Cooling system
PL-014612 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014614 |  | B | P | 18.1:TZ-MID-68-WPR2-207138 & TZ-MID-68-WPR2-207142 - Trunnion to be welded to Structure | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014615 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014616 |  | B | P | 18.3:Paint touch up to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-014618 |  | B | P | 18:PS5-60-UR-8100D_TP-843 - F-1 Equpiment joint Flange Management up to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014619 |  | B | P | 18.1:1" valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014620 |  | B | P | 18.2:TZ-MID-68-WPR2-207192 & TZ-MID-68-WPR2-207195 - Trunnion to be welded to Structure | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014621 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014622 |  | B | P | 18.4:Paint touchup to be done | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014623 |  | B | P | 18:PS5-60-UR-8100D_TP-845 - F-1 Equpiment joint Flange Management up to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014624 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014625 |  | B | P | 18.2:TZ-MID-68-WPR2-207184 & TZ-MID-68-WPR2-207187 - Trunnion to be welded to Structure | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014626 |  | B | P | 18.3:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014627 |  | B | P | 18.4:Paint touchup to be done | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014628 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014629 |  | B | P | 18.1:TZ-MID-68-WPR2-207202 & TZ-MID-68-WPR2-207206 - Trunnion to be welded to Structure | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014630 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014631 |  | B | P | 18.3:Paint touchup to be done | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014632 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014633 |  | B | P | 18.1:TZ-MID-68-WPR2-207197 & TZ-MID-68-WPR2-207201 - Trunnion to be welded to Structure | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014634 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014635 |  | B | P | 18.3:Paint touchup to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014636 | PS5-01-UZ-610 | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-01-11 - Inergen for Power Gen Building
PL-014637 | PS5-01-UZ-610 | C | M | 8.1:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-01-11 - Inergen for Power Gen Building
PL-014638 | PS5-01-UZ-610 | B | M | 10:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-01-11 - Inergen for Power Gen Building
PL-014639 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014640 |  | B | P | 18.1:TZ-MID-68-WPR2-208746 & TZ-MID-68-WPR2-208747 - Equpiment joint Flange Management up to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014641 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014642 |  | C | P | 18.3:Paint touchup to be done | Completed |  | PS5-60-73 - Engine D Cooling system
PL-014643 | PS5-60-TG-0005D | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014654 | PS5-60-TG-0006D | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014655 | PS5-60-TG-0007D | B | I | Permanent tags and hanging tags to be installed | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014656 | PS5-60-TG-0008D | B | I | Permanent tags and hanging tags to be installeds | Originated |  | PS5-60-73 - Engine D Cooling system
PL-014686 | PS5-60-IE-0002A-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014688 | PS5-60-IE-0002A-CC03 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014691 | PS5-60-IE-0003A-CC26 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014693 | PS5-60-IN-0002A-CC04 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP)
PL-014694 | PS5-60-LA-0002A-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014695 | PS5-60-LA-0002A-CC02 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014696 | PS5-60-LA-0002A-CC03 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014697 | PS5-60-BI-0006B-CC02 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014698 | PS5-60-BI-0006B-CC03 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014699 | PS5-60-BI-0006B-CC04 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014700 | PS5-60-36_SS_ALL_LINES | C | P | 6:COLOUUR CODE AND MARKING TO BE DONE | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-014701 | PS5-60-35_SS_ALL_LINES | C | P | 6:COLOUR CODE AND MARKING TO BE DONE | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-014702 | PS5-60-BI-0006B-CC05 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014703 | PS5-60-BI-0006B-CC06 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014704 | PS5-60-IE-0002B-CC05 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-04 - Power Generation Package B
PL-014705 | PS5-60-IN-0002B-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014706 | PS5-60-IN-0002B-CC02 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014707 | PS5-60-IN-0002B-CC03 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014708 | PS5-60-35_SS_ALL_LINES | B | P | 6:RING ISTALLED-WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-014709 | PS5-60-36_SS_ALL_LINES | B | P | 6:RING INSTALLED-WIREMESH TO BE INSTALLED | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-014710 | PS5-60-42_SS_ALL_LINES | C | P | 6:COLOUR CODING AND MARKING TO BE DONE | Originated |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-014711 | PS5-60-43_SS_ALL_LINES | C | P | 6:COLOUR CODE AND MARKING TO BE DONE | Originated |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-014713 | PS5-60-43_SS_ALL_LINES | B | P | 6.1:TP-211- TOPCOAT TOUCHUP TO BE DONE | Originated |  | PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B
PL-014714 | PS5-60-42_SS_ALL_LINES | B | P | TOP COAT TOUCHUP TO BE DONE | Originated |  | PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A
PL-014849 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-014851 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-014853 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-38 - Injector Tip Cooling Module D
PL-014854 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-60-38 - Injector Tip Cooling Module D
PL-014858 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-014859 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-014862 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Completed |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-014864 |  | B | P | 18.1:Paint touchup to be done | Completed |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-014868 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-014869 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-014875 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-014877 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-014886 |  | B | P | 18:Paint touchup to be done | Completed |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-014893 |  | A | P | 18:Collection Pot Connection & Installation to be done | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-014894 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-014898 |  | A | P | 18:Collection Pot Connection & Installation to be done | Originated |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-014901 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-014904 | PS5-60-BE-0026B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-71 - Engine B Cooling system
PL-014905 | PS5-60-BE-0027B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014906 | PS5-60-BE-0028B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-014907 |  | B | P | 18:Paint touchup to be done | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-014908 | PS5-60-IE-0002B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-04 - Power Generation Package B
PL-014909 | PS5-60-IE-0003B-CD14 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-04 - Power Generation Package B
PL-014910 | PS5-60-IE-0003B-CL01 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-014911 | PS5-60-IH-0001A-CL05 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs
PL-014912 | PS5-60-IH-0001B-CL05 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs
PL-014913 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-71-04 - CFO Storage Tank
PL-014914 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-71-04 - CFO Storage Tank
PL-014915 | PS5-60-IN-0002B-CL02 | B | E | Earthing Tag of the cable gland shall be connected to the earthing stud/bar at both side | Originated |  | PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP)
PL-014918 |  | B | P | 18:PS5-71-TR-4100_N1& N16, PS5-71-SPZQ-0069 - Flange Management to be done | Originated |  | PS5-71-04 - CFO Storage Tank
PL-014919 |  | B | P | 18.1:Paint touchup to be done | Originated |  | PS5-71-04 - CFO Storage Tank
PL-014925 | PS5-60-BI-0008A-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014926 | PS5-60-BI-0008A-CC02 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014927 | PS5-60-BI-0008B-CC01 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014931 | PS5-60-BI-0008B-CC02 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-01 - Power Generation Package A
PL-014953 | PS5-60-IE-0003A-CC10 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014954 | PS5-60-IE-0003A-CC11 | B | I | internal Grounding not yet Done | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-014955 | PS5-60-IE-0003A-CC16 | B | I | internal Grounding not yet Done | Completed |  | PS5-60-02 - Power Gen Package A (UCP)
PL-015094 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-015095 |  | B | P | 18:TZ-MID-68-WPR2-206109 - Flange Insulation Set PS5-28-SPZZ-0023 Flange management to be done | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-015096 |  | B | P | 18:TZ-MID-68-WPR2-206094 - Flange Insulation Set PS5-28-SPZZ-0024 Flange management to be done | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-015097 |  | B | P | 18:TZ-MID-68-WPR2-206304 - Pressure Instrument PS5-28-SDV-0045 Flange management to be done | Originated |  | PS5-28-17 - Reinjection Pump
PL-015098 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed. | Originated |  | PS5-28-17 - Reinjection Pump
PL-015099 |  | B | P | 18:PS5-71--TR-4200_N2 - F15 Flange management to be done | Originated |  | PS5-71-12 - CFO Service Tank
PL-015100 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-28-09 - Observation Basin
PL-015101 |  | B | P | 18:TZ-MID-68-WPR2-208395 - Civil structure to be installed & GL02 welding to be done after structure instalation | Originated |  | PS5-28-17 - Reinjection Pump
PL-015148 | PS5-60-BE-0004A-CC01 | B | I | PS5-60-IN-0001A TB 100 X2 11, 12 NOT TERMINATED DWG ISSUE | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-015149 | PS5-60-BI-0017B-CC02 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-015150 | PS5-60-IE-0003B-CC05 | B | I | PS5-60-IE-0001B TB Numbers 25,8,0,1,4,5,14,49 NOT AVAILBUL IN THE PANEL | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015151 | PS5-60-IN-0001A-CC02 | B | I | JB - PS5-60-BE-0004A TB XI 3,4 NOT TERMINATED DWG ISSUE | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-015152 | PS5-60-IN-0001A-CC04 | B | I | JB - PS5-60-BE-0004A TB XI 14,15,16 NOT TERMINATED DWG ISSUE | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-015206 |  | B | P | 18: CONN. TO PS4-60-PA-3400/SN EQUIPMENT NOZZLE CONNECTION TO BE DONE AFTER GALT | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-015306 | PS5-01-BI-1118-CC01 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015307 | PS5-25-BI-1102-CC01 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015308 | PS5-25-BI-1115-CC01 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015309 | PS5-28-BI-1105-CC01 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015310 | PS5-50-BI-1107-CC01 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015311 | PS5-60-IE-0003B-CC06 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015312 | PS5-60-IE-0003B-CC07 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015313 | PS5-60-IE-0003B-CC08 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015314 | PS5-60-IE-0003B-CC08 | B | I | TB X1101 - TB 31,32,33,34 CORE NOT TERMIANTED | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015315 | PS5-60-IE-0003B-CC09 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015316 | PS5-60-IE-0003B-CC15 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015317 | PS5-60-IE-0003B-CC16 | B | I | Grounding between Gland to Gland not yet Installed | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015335 | PS5-60-DM-3400-CL01 | B | E | Tags are not available ( Ferrule ) | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-015336 | PS5-60-IES-3400-CD01 | B | E | Tags are not available ( Ferrule ) | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-015341 | PS5-03-BI-1512-CC01 | B | I | Tags are not available ( Ferrule ) | Originated |  | PS5-03-09 - FZ-09 - Power Generation Building - Engine Bay 1
PL-015345 | PS5-60-IE-0003B-CC23 | B | I | Tags are not available ( Ferrule ) | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015346 | PS5-60-IE-0003B-CC24 | B | I | Tags are not available ( Ferrule ) | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015347 | PS5-71-IN-0003-CC05 | B | I | Tags are not available ( Ferrule ) | Originated |  | PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP)
PL-015354 | PS5-01-BI-1515-CC01 | B | I | Tags are not available ( Ferrule ) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015355 | PS5-01-BI-1520-CC01 | B | I | Tags are not available ( Ferrule ) | Originated |  | PS5-01-10 - Water Mist Package
PL-015357 | PS5-60-IE-0003B-CC23 | B | I | No proper earth clamp for armour | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015358 | PS5-60-IE-0003B-CC24 | B | I | No proper earth clamp in the armour | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015380 | PS5-02-SAS-0003 | B | M | 4:The clamp is not properly installed | Originated |  | PS5-02-01 - Miscellaneous Safety equipment
PL-015381 | PS5-02-SAS-0004 | B | M | 4:The clamp is not properly installed | Originated |  | PS5-02-01 - Miscellaneous Safety equipment
PL-015382 | PS5-02-SAS-0006 | B | M | 4:During inspection, the clamp support was found broken. | Originated |  | PS5-02-01 - Miscellaneous Safety equipment
PL-015383 | PS5-02-SCA-0001 | C | M | 4:During inspection, it was found that the packing list specifies 1 No. of 7 kg portable carbon dioxide fire extinguisher with cabinet, but 6 Nos. were received. ( 5 nos overage). | Originated |  | PS5-02-02 - Portable Fire Fighting Equipments
PL-015384 | PS5-02-SCA-0001 | C | M | 4.1:During inspection, 4 Nos. of 9 L foam fire extinguishers were found inside the box; they are not listed in the packing list. | Originated |  | PS5-02-02 - Portable Fire Fighting Equipments
PL-015386 | PS5-28-HE-2200 | C | M | 4:AS PER THE PACKING LIST 4 nos BUT RECEIVED 7 Nos (OVERAGE 3 nos) | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-015387 | PS5-28-HE-2200 | C | M | 4.1:FOUND 1 no KNOB WHICH IS NOT SHOWING IN PACKING LIST (1 no OVERAGE) | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-015402 | PS5-01-BI-2520-CC01 | B | I | Ferulle tags missing | Originated |  | PS5-01-10 - Water Mist Package
PL-015403 | PS5-01-BI-2520-CC01 | B | I | Clamp for screen shield not installed | Originated |  | PS5-01-10 - Water Mist Package
PL-015492 |  | B | P | 18:PS5--25-PIT-1102 - TZ-MID-68-WPR2-206085, Pressure Instrument Flange management to be done | Originated |  | PS5-25-01 - Export Pipeline Pig Receiver
PL-015504 |  | B | P | 18:PS5--25-ZS-1201 - TZ-MID-68-WPR2-206088, Pressure Instrument Flange management to be done | Originated |  | PS5-25-07 - Export Pipeline Pig Launcher
PL-015508 |  | B | P | 18:TZ-MID-68-WPR2-206157 - Valve handle orientation not as per ISO Drawing RLMU to be done | Originated |  | PS5-25-07 - Export Pipeline Pig Launcher
PL-015509 |  | B | P | 18:PS5-60-UR-8100E_TP-869 & TP_870 - Hose connection joint FM to be done | Originated |  | PS5-60-39 - Injector Tip Cooling Module E
PL-015510 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-39 - Injector Tip Cooling Module E
PL-015511 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-39 - Injector Tip Cooling Module E
PL-015514 |  | B | P | 18:PS5-60-UR-8100F_TP-888 & TP_890 - Equpiment connection Flange Management to be done | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-015515 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-015516 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F
PL-015517 |  | B | P | 18:PS5-71-TR-4100_N5 - F1 Flange Management to be done after GALT test | Originated |  | PS5-71-05 - CFO Transfer Pump A/B
PL-015518 |  | B | P | 18.1: PS5-71-SPXA-0002 - Bund wall Pipe penetration seal to be fixed | Originated |  | PS5-71-05 - CFO Transfer Pump A/B
PL-015519 |  | B | P | 18.2:PS5-71-PA-3300A & 3300B - Pump connection Flange Management to be done | Originated |  | PS5-71-05 - CFO Transfer Pump A/B
PL-015521 |  | A | P | 18:PS5-28-TIT-1104 & PS5-28-TIT-1105 - Temperature instrument to be install & Flange Management to be done | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-015522 |  | B | P | 18:TZ-MID-68-WPR2-206309 - Lever/Handl wheel OR I= South, RLMU to be done | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-015523 |  | B | P | 18.1:TZ-MID-68-WPR2-206202 - Lever/Handl wheel OR I= UP, RLMU to be done | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-015551 | PS5-01-BI-1117-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015553 | PS5-01-BI-1117-CC01 | B | I | Screen armour clamp not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015555 | PS5-71-DM-3500A-CL01 | B | E | Ferrule tags not available | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-015570 |  | B | P | 18: | Originated |  | PS5-25-07 - Export Pipeline Pig Launcher
PL-015571 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015572 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-74 - Engine E Cooling system
PL-015573 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015574 |  | B | P | 18.1:PS5-60-UR-8100F_TP-884 & 886 - Equpiment joint Flange Management up to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015575 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-75 - Engine F Cooling system
PL-015577 | PS5-71-IES-3500A-CD01 | B | E | FERULLE TAGS MISSING | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-015580 | PS5-71-IES-3500B-CD01 | B | E | FERULLE TAGS NOT AVAILABLE | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-015581 | PS5-71-DM-3500B-CL01 | B | E | FERRULE TAGS NOT AVAILABLE | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-015584 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015585 |  | B | P | 18.1:PS5-60-UR-8100F_TP-887 - Equpiment joint Flange Management up to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015586 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-75 - Engine F Cooling system
PL-015587 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015588 |  | B | P | 18.1:PS5-60-UR-8100F_TP-885 - Equpiment joint Flange Management up to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015589 |  | B | P | 18.2:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-75 - Engine F Cooling system
PL-015592 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015594 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015595 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-75 - Engine F Cooling system
PL-015596 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-75 - Engine F Cooling system
PL-015597 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-71-17 - Diesel Fuel Distribution Header
PL-015598 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-71-17 - Diesel Fuel Distribution Header
PL-015603 | PS5-01-BI-2110-CC01 | B | I | FERRULE TAGS NOT AVAILABLE | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015604 | PS5-01-BI-2110-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015656 | PS5-03-BI-2514-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015657 | PS5-03-BI-2514-CC01 | B | I | Clamp support not available for screen shield | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015658 | PS5-71-IN-0001-CC10 | B | I | Ferrule tags not available | Originated |  | PS5-71-19 - Diesel Separator Module (UCP)
PL-015659 | PS5-71-IN-0001-CC10 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-71-19 - Diesel Separator Module (UCP)
PL-015660 | PS5-71-IN-0001-CC08 | B | I | Ferrule tags not available | Originated |  | PS5-71-19 - Diesel Separator Module (UCP)
PL-015661 | PS5-71-IN-0001-CC08 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-71-19 - Diesel Separator Module (UCP)
PL-015662 | PS5-60-49_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-015663 | PS5-60-50_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-015664 | PS5-60-70_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-70 - Engine A Cooling system
PL-015665 | PS5-60-71_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-71 - Engine B Cooling system
PL-015696 | PS5-60-IE-0003A-CC23 | B | I | Ferrule tags not available | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-015697 | PS5-60-IE-0003A-CC23 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-015698 | PS5-60-IE-0003A-CC24 | B | I | Ferrule tags not available | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-015699 | PS5-60-IE-0003A-CC24 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-015701 | PS5-01-UZ-610 | A | M | 10.1:Nitrogen (N₂) cylinders received with low filling pressure. As per the packing list, the required pressure is 200 bar, but two cylinders were received at only 1300 psi (89.6 bar).Replace or refill the cylinders to the specified 200 bar pressure. | Originated |  | PS5-01-11 - Inergen for Power Gen Building
PL-015705 | PS5-60-IE-0003B-CC23 | B | I | Ferrule tags are not available | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015706 | PS5-60-IE-0003B-CC23 | B | I | Clamp and support for screen shiled not available | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015714 |  | B | P | 18:PS5-60-PA-3300/SN - Flange Management to be done after pump alignment | Completed |  | PS5-60-24 - Cooling Water Tank & Pump
PL-015715 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-24 - Cooling Water Tank & Pump
PL-015727 | PS5-60-DM-3300-CL01 | B | E | Ferrule tags not available | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-015728 | PS5-60-IES-3300-CD01 | B | E | Ferrule tags not available | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-015729 |  | B | P | 18:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-015730 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-24 - Cooling Water Tank & Pump
PL-015731 |  | B | P | 18:TZ-MID-68-WPR2-206949 - PS5-SPS-A550-401, Support to be installed | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015732 |  | B | P | 18.1:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-74 - Engine E Cooling system
PL-015733 |  | B | P | 18:Valve Lever/Handle Wheel ORI=W, RLMU to be done | Originated |  | PS5-01-02 - Fire Water Pump A
PL-015734 |  | B | P | 18:Valve Lever/Handle Wheel ORI=W, RLMU to be done | Originated |  | PS5-01-03 - Fire Water Pump B
PL-015736 | PS5-03-SEA-0003-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-015738 | PS5-03-SEA-0003-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-015741 | PS5-60-SEA-0001-CC18 | B | I | Ferrule tgas not available | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-015742 | PS5-60-SEA-0001-CC18 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-015743 | PS5-03-SFMC-0006-CC01 | C | I | Missing core marker | Originated |  | PS5-04-05 - 33kV SIS/FGS System
PL-015744 | PS5-04-PMC-0002-CS03 | C | E | Missing cable tag | Originated |  | PS5-04-04 - 33kV PCS System
PL-015745 | PS5-04-PMC-0008-CC26 | C | I | Missing core marker PS5-04-PMC-0008-CC26/TBA12/5/PR01/WH at PMC-0008 side | Originated |  | PS5-04-04 - 33kV PCS System
PL-015746 | PS5-04-PMC-0008-CC26 (Reconnection) | C | I | Missing core marker PS5-04-PMC-0008-CC26/TBA12/5/PR01/WH at PMC-0008 side | Originated |  | PS5-04-04 - 33kV PCS System
PL-015747 | PS5-61-IK-0001-CC29 (Reconnection) | C | I | Missing core marker PS5-61-IK-0001-CC29/TBD09/5/PR03/WH at PMC-0007 side | Originated |  | PS5-04-04 - 33kV PCS System
PL-015748 | PS5-61-IK-0001-CC64 (Reconnection) | B | I | To changed terminal block name following interconnection drawing | Originated |  | PS5-04-04 - 33kV PCS System
PL-015749 | PS5-61-IK-0001-CC65 (Reconnection) | B | I | To changed terminal block name following interconnection drawing | Originated |  | PS5-04-04 - 33kV PCS System
PL-015756 | PS5-03-SEA-0003-CJ01 | B | I | Ferrule tags not available | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-015757 | PS5-03-SEA-0003-CJ01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-015783 | PS5-60-IE-0003A-CC22 | B | I | Ferrule tags not available | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-015784 | PS5-60-IE-0003A-CC22 | B | I | Clamp and support for screen shield are not available | Originated |  | PS5-60-02 - Power Gen Package A (UCP)
PL-015786 | PS5-71-IN-0001-CC09 | B | I | Ferrule tags are not available | Originated |  | PS5-71-19 - Diesel Separator Module (UCP)
PL-015787 | PS5-71-IN-0001-CC09 | B | I | Clamp and support for screen shield are not available | Originated |  | PS5-71-19 - Diesel Separator Module (UCP)
PL-015839 | PS5-06-GU-0003A-CD01 | B | E | Ferrule tags not available | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-015840 | PS5-06-IG-0004A-CD01 | B | E | Ferrule tags not available | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-015841 |  | B | P | 18.1:TZ-MID-68-WPR2-2073653 - ITEM 03, LEVER/HANDWHEEL ORI = W,RLMU to be done | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-015842 |  | B | P | 18.2:Pickling & Passivation to be done in affected area | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-015843 | PS5-06-GU-0003B-CD01 | B | E | Ferrule tag not available | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-015844 | PS5-06-IG-0004B-CD01 | B | E | Ferrule tags not available | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-015845 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-40 - Injector Tip Cooling Module F
PL-015846 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E
PL-015847 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F
PL-015848 | PS5-06-GU-0003B-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-015849 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F
PL-015850 |  | B | P | 18:PS5-60-PPA-3400/DN - F1 & F2 Flange management to be done after pump alignment | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-015851 |  | B | P | 18.1:Pickling & Passivation to be done in affected area | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-015852 | PS5-06-GU-0003A-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-015864 | PS5-71-IN-0002-CC07 | B | I | Ferrule tags not available | Originated |  | PS5-71-09 - CFO Pre-Pressure Modules (UCP)
PL-015865 | PS5-09-ACU-0007_OUTDOOR_INSTALLATION | B | M | 10:STRUCTURAL UNCOATED BOLTS TO BE REPLACED | Completed |  | PS5-09-05 - HVAC for EITS Building
PL-015866 | PS5-09-ACU-0007_OUTDOOR_INSTALLATION | B | H | 17:STRUCTURAL UNCOATED BOLTS TO BE REPLACED | Originated |  | PS5-09-05 - HVAC for EITS Building
PL-015887 | PS5-60-26_SS_ALL_LINES | C | P | 6:COLOUR CODE AND MARKING TO BE DONE | Originated |  | PS5-60-26 - Instrument Air Compressor Skid
PL-015923 |  | B | P | 18:Pickling & Passivation to be done in affected area | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-015924 | PS5-01-BI-0002-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-01-10 - Water Mist Package
PL-015925 | PS5-01-BI-0002-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-01-10 - Water Mist Package
PL-015926 |  | B | P | 18:PS5-60-UR-8100E_TP-863 & 865 - Hose connection joint FM to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015927 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015928 | PS5-01-BI-0003-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-01-10 - Water Mist Package
PL-015929 | PS5-01-BI-0003-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-01-10 - Water Mist Package
PL-015930 | PS5-01-BI-0004-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-01-10 - Water Mist Package
PL-015931 |  | B | P | 18:PS5-60-UR-8100E_TP-866 - Hose connection joint FM to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015932 |  | B | P | 18.1:CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015933 | PS5-01-BI-0004-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-01-10 - Water Mist Package
PL-015935 |  | B | P | 18:PS5-60-UR-8100E_TP-864 - Hose connection joint FM to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015936 |  | B | P | 18.1:1" Valve CTR commodity code to be add. RLMU to be done | Originated |  | PS5-60-74 - Engine E Cooling system
PL-015937 | PS5-01-LIT-4201-CJ01 | B | I | ferulle tags not available | Originated |  | PS5-01-10 - Water Mist Package
PL-015938 | PS5-01-LIT-4201-CJ01 | B | I | Clamp and support arenot available | Originated |  | PS5-01-10 - Water Mist Package
PL-015939 |  | B | P | 18:PS5-71-TR-4200_N3 - Tank joint F1 Flange Management to be done | Originated |  | PS5-71-13 - CFO Service Pump A/B
PL-015940 |  | B | P | 18.1:PS5-71-PA-3400A_SN & PS5-71-PA-3400B_SN - Pump connection Flange Management to be done | Originated |  | PS5-71-13 - CFO Service Pump A/B
PL-015941 | PS5-60-IE-0003B-CC22 | B | I | Ferrule tags not available | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015942 | PS5-60-IE-0003B-CC22 | B | I | Clamp and support are not available | Originated |  | PS5-60-05 - Power Gen Package B (UCP)
PL-015943 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-015946 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-39 - Injector Tip Cooling Module E
PL-015947 |  | B | P | 18:GL01 PTFE Isolation Pad to be Fixed | Completed |  | PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E
PL-015948 | PS5-61-IV-0002A | A | E | Cables to be connected after the gland plate change | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-015949 | PS5-61-IV-0002B | A | E | Cables to be connected after the gland plate change | Originated |  | PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001)
PL-015952 | PS5-71-BI-2306-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015955 | PS5-71-BI-2314-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015956 | PS5-71-BI-2314-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015960 | PS5-71-BI-1306-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015961 | PS5-71-BI-1306-CC01 | B | I | Clamp and support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015964 | PS5-71-BI-1116-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015965 | PS5-03-SEA-0003-CC01 | C | I | WIRE MARKER MISSING | Originated |  | PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room
PL-015966 | PS5-71-BI-1116-CC01 | B | I | Clamp and support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-015999 | PS5-71-BI-2107-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016000 | PS5-71-BI-2107-CC01 | B | I | Clamp and support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016005 | PS5-71-BI-1109-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016007 | PS5-71-BI-1109-CC01 | B | I | Clamp and support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016029 | PS5-60-UZ-8200A | B | M | PRESSURE GAUGE TO BE FIXED | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-016031 | PS5-25-BI-2105-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016032 | PS5-25-BI-2105-CC01 | B | I | Clamp and support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016033 | PS5-25-BI-1115-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016034 | PS5-25-BI-1115-CC01 | B | I | Clamp and support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016045 | PS5-60-TR-4300 | C | M | 3:FINAL TOUCH UP PAINT TO BE CARRIED OUT | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-016046 | PS5-60-TR-4400 | C | M | 3:FINAL TOUCH UP PAINT TO BE CARRIED OUT | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-016115 | PS5-60-PA-3400 | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-016116 | PS5-60-PA-3300 | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-016120 | PS5-01-PA-3200A | B | M | 21 COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-016121 | PS5-01-PA-3200B | B | M | 21:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO- RUN | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-016122 | PS5-28-PA-3700A | C | M | 14:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-016123 | PS5-28-PA-3700B | C | M | 14:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-016124 | PS5-60-51_SS_ALL_LINES | B | P | 6: Wire Mesh to be installed | Originated |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-016125 | PS5-60-52_SS_ALL_LINES | B | P | 6:wire mesh to be installed | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-016126 | PS5-28-PA-3400 | C | M | 21:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-016129 | PS5-25-BI-2201-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016130 | PS5-25-BI-2201-CC01 | B | I | Clamp ang support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016131 | PS5-25-BI-2203-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016132 | PS5-25-BI-2203-CC01 | B | I | Clamp and support not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016133 | PS5-25-BI-2205-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-25-01 - Export Pipeline Pig Receiver
PL-016134 | PS5-25-BI-2205-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-25-01 - Export Pipeline Pig Receiver
PL-016135 | PS5-25-BI-2309-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016136 | PS5-25-BI-2309-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016137 | PS5-25-BI-2106-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016138 | PS5-25-BI-2106-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016139 | PS5-25-BI-2308-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016140 | PS5-25-BI-2308-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016141 | PS5-25-BI-2316-CC01 | B | I | Ferrule tags not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016142 | PS5-25-BI-2316-CC01 | B | I | Clamp and support for screen shield not available | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016251 | PS5-60-UZ-8200B | B | M | PRESSURE GAUGE TO BE FIXED | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-016307 | PS5-28-PA-3700A | B | M | 14.1:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-016309 | PS5-28-PA-3700B | B | M | 14.1:COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-016516 | PS5-60-TR-4300 | B | M | NAME PLATE TO BE INSTALLED | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-016517 | PS5-60-TR-4400 | B | M | NAME PLATE TO BE INSTALLED | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-016518 | PS5-60-UZ-8200A | B | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | Originated |  | PS5-60-35 - Injector Tip Cooling Module A
PL-016519 | PS5-60-UZ-8200B | B | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | Originated |  | PS5-60-36 - Injector Tip Cooling Module B
PL-016541 | PS5-28-02_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-28-02 - Closed Drain Header 2
PL-016542 | PS5-60-37_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-016543 | PS5-60-38_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-016545 | PS5-60-72_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-72 - Engine C Cooling system
PL-016546 | PS5-60-73_SS_ALL_LINES | B | P | 6:WIRE MESH TO BE INSTALLED | Originated |  | PS5-60-73 - Engine D Cooling system
PL-016568 | PS5-06-GU-0003A | B | E | 'CH1+A2 - 2 extract fan metallic covers on top of cubicle are missing | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016569 | PS5-06-GU-0003A | B | E | 'CH1+A2 - Fan M8 not working | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016573 | PS5-06-GU-0003A | C | E | 'CH1+A2 - terminal bloc number and terminal number for T40_1 missing | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016574 | PS5-06-GU-0003A | B | E | 'INP1+A1 - 2 canbus Cat6 RJ45 cable betwwen UPS and Battery are missing - refer to SLD TZ-MID-60-RME2-150011 | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016576 | PS5-06-GU-0003A | C | E | 'CH1+A2 - terminal block number for T40_2 missing | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016577 | PS5-06-GU-0003A | C | E | 'CH1+A2 - X943 not shown in wiring diagram | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016578 | PS5-60-01_SS_ALL_LINES | C | P | 6.1:Colour code and marking to be done | Originated |  | PS5-60-01 - Power Generation Package A
PL-016579 | PS5-06-GU-0003B | C | E | 'CH2+A7 - terminal block number for T40_2 interface missing | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016580 | PS5-06-GU-0003A | C | E | 'CH2+A7 - terminal block number for T40_2 interface missing | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016581 | PS5-60-04_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-04 - Power Generation Package B
PL-016582 | PS5-60-04_SS_ALL_LINES | C | P | 6.1: Stenciling to be done | Originated |  | PS5-60-04 - Power Generation Package B
PL-016584 | PS5-60-27_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-016585 | PS5-60-27_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-27 - Compressed Air Starting Skid
PL-016587 | PS5-60-49_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-016588 | PS5-60-49_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A
PL-016589 | PS5-60-50_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-016590 | PS5-60-50_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B
PL-016591 | PS5-60-56_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-016592 | PS5-60-56_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-016596 | PS5-60-58_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-016597 | PS5-60-58_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-016598 | PS5-60-70_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-70 - Engine A Cooling system
PL-016599 | PS5-60-70_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-70 - Engine A Cooling system
PL-016600 | PS5-60-71_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-71 - Engine B Cooling system
PL-016601 | PS5-60-71_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-71 - Engine B Cooling system
PL-016603 | PS5-71-20_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-016604 | PS5-71-20_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-71-20 - Diesel Fuel Day Tank
PL-016606 | PS5-71-21_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-016607 | PS5-71-21_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-71-21 - Diesel Transfer Pump A/B
PL-016608 | PS5-71-22_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-016610 | PS5-71-22_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-71-22 - Diesel Fuel Pre Pressure Module
PL-016614 |  | B | P | 18:TZ-MID-68-WPR2-208480 - ITEM 05, BALL VALVE , 316/316L SS A182-F316/F316L , CL300 RLMU to be done | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-016615 |  | B | P | 18.1:TZ-MID-68-WPR2-208480 - Item 06 / PS5 60 LIT-4301, LEVEL INSTRUMENT to be install | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-016616 |  | B | P | 18:TZ-MID-68-WPR2-208483 - ITEM 05, Ball Valve, CL300 RLMU tobe done | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-016617 |  | B | P | 18.1:TZ-MID-68-WPR2-208483 - Item 06 / PS5 60 LIT-4401 , LEVEL INSTRUMENT to be install | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-016620 | PS5-06-GU-0003A | B | E | 'INV1+A3 - Resistor -R11 & R14 are damaged - precharge xircuit not working | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016621 | PS5-06-GU-0003B | B | E | 'INV2+A8 - Resistor -R11 & R14 are damaged - precharge xircuit not working | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016622 | PS5-06-GU-0003B | B | E | 'INV2+A8 - internal wiring from X981 to A89 missing along with the connector at A89 | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016623 | PS5-06-GU-0003A | B | E | 'INV1+A3 - interpanel wiring to link X990 in INV1 to X990 in CH2 is missing | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016624 | PS5-06-GU-0003A | B | E | 'CH1+A2 - interpanel wiring to link T40_2 from CH1 to CH2 is missing | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016625 | PS5-28-PA-3400 | B | M | 14: COUPLING SPACER TO BE TIGHTENED PROPERLY AFTER MOTOR SOLO-RUN BY COMMISSIONING | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-016626 | PS5-28-PA-3400 | C | M | 14.1:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-016627 | PS5-06-GU-0003A | B | E | 'CH1+A2 - Relay settings for DC Earth Fault to be provided | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016628 | PS5-06-GU-0003B | B | E | 'CH2+A7 - Relay settings for DC Earth Fault to be privided | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016629 | PS5-06-GU-0003A | C | E | 'Load Bank breaker Q8 is connected at -Q6 UPS side and not battery side | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016630 | PS5-06-GU-0003A | C | E | 'Wiring diagram rev 7 from factory has been submitted to EACOP whereas Vendor is having rev 10 available | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016631 | PS5-06-GU-0003A | B | E | 'Wiring TZ-MID-60-RME2-150013 To be updated | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016632 | PS5-06-GU-0003B | B | E | 'INV2+A8 - door closing mechanism damaged | Originated |  | PS5-06-02 - AC UPS - Power Generator Building
PL-016633 | PS5-28-PA-3400 | C | M | 14.2:EARTHING TO BE DONE | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-016643 | PS5-60-VA-5100B | B | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | Originated |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-016644 | PS5-60-VA-5100C | C | M | SKID DRAINS NEED TO BE INSTALLED ELBOW | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-016645 | PS5-60-VA-5100D | C | P | SKID DRAINS NEED TO BE INSTALLED ELBOW | Originated |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-016646 | PS5-71-18_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-71-18 - Diesel Separator Module
PL-016647 | PS5-71-18_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-71-18 - Diesel Separator Module
PL-016649 | PS5-60-29_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-016650 | PS5-60-29_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Completed |  | PS5-60-29 - Air Receiver B & Air Regulator B
PL-016651 | PS5-60-28_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-28 - Air Receiver A & Air Regulator A
PL-016652 | PS5-60-28_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-28 - Air Receiver A & Air Regulator A
PL-016658 | PS5-01-PA-3100A | C | M | 21:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | Originated |  | PS5-01-02 - Fire Water Pump A
PL-016670 | PS5-01-PA-3100B | C | M | 21:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQIUPMENT | Originated |  | PS5-01-03 - Fire Water Pump B
PL-016671 | PS5-01-PA-3100B | A | P | 21.1:PRESSURE SENCING LINE TO BE INSTALLED | Originated |  | PS5-01-03 - Fire Water Pump B
PL-016673 | PS5-01-PA-3100B | A | M | 21.2:PRESSURE GAUGE TO BE RE-INSTALLED | Originated |  | PS5-01-03 - Fire Water Pump B
PL-016675 | PS5-01-PA-3100A | A | P | 21.1:PRESSURE SENCING LINE TO BE INSTALLED | Originated |  | PS5-01-02 - Fire Water Pump A
PL-016676 | PS5-01-PA-3100A | A | M | 21.2:PRESSURE GAUGE TO BE RE-INSTALLED | Originated |  | PS5-01-02 - Fire Water Pump A
PL-016740 | PS5-03-BI-2506-CC01 | C | I | No Indoor Cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016743 | PS5-03-BI-2506-CC01 | B | I | No Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016747 | PS5-03-BI-2506-CC01 | B | I | MCT packing is not Proper | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016749 | PS5-03-BI-2506-CC01 | B | I | No Proper Screen Earthing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016751 | PS5-03-BI-2506-CC01 | C | I | No Outdoor Metal Cable Tag | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016758 | PS5-03-BI-2515-CC01 | C | I | No indoor Cable Tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016761 | PS5-03-BI-2515-CC01 | B | I | No Core Markers | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016763 | PS5-03-BI-2515-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016767 | PS5-03-BI-2515-CC01 | B | I | No proper MCT packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016770 | PS5-03-BI-2515-CC01 | C | I | No outdoor Metal Cable Tag | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016780 | PS5-25-BI-1302-CC01 | C | I | No Indoor Cable Tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016782 | PS5-25-BI-1302-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016784 | PS5-25-BI-1302-CC01 | B | I | No Proper MCT packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016788 | PS5-25-BI-1302-CC01 | B | I | No core Markers | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016789 | PS5-25-BI-1302-CC01 | C | I | No outdoor Metal Cable Tag | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016794 | PS5-25-BI-1310-CC01 | C | I | No Indoor Cable Tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016795 | PS5-25-BI-1310-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016796 | PS5-25-BI-1310-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016797 | PS5-25-BI-1310-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016798 | PS5-25-BI-2104-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016799 | PS5-25-BI-2104-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016800 | PS5-25-BI-2104-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016801 | PS5-25-BI-2108-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016802 | PS5-25-BI-2108-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016803 | PS5-25-BI-2109-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016804 | PS5-25-BI-2109-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016805 | PS5-25-BI-2109-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016806 | PS5-28-BI-1307-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016807 | PS5-28-BI-1307-CC01 | B | I | No Core Markers | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016808 | PS5-71-BI-1110-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016809 | PS5-71-BI-1110-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016810 | PS5-71-BI-1110-CC01 | B | I | Missing Cable’s some Core Markers | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016811 | PS5-71-BI-1113-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016813 | PS5-71-BI-1113-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016814 | PS5-71-BI-1113-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016815 | PS5-71-BI-1117-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016816 | PS5-71-BI-1117-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016817 | PS5-71-BI-2113-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016818 | PS5-71-BI-2113-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016819 | PS5-71-BI-2114-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016820 | PS5-71-BI-2114-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016821 | PS5-71-BI-2114-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016831 | PS5-71-BI-2115-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016832 | PS5-60-24_SS_ALL_LINES | C | P | 6:Stenciling to be done | Originated |  | PS5-60-24 - Cooling Water Tank & Pump
PL-016833 | PS5-71-BI-2115-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016834 | PS5-60-25_SS_ALL_LINES | C | P | 6:Stenciling to be done | Originated |  | PS5-60-25 - Cooling Water Maintenance Tank & Return Pump
PL-016835 | PS5-60-56_SS_ALL_LINES | B | P | 16:VALVE,FLANGE AND PENETRATION LOCATION TO BE DONE | Originated |  | PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A
PL-016836 | PS5-71-BI-2118-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016837 | PS5-71-BI-2118-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016838 | PS5-71-BI-2118-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016839 | PS5-71-BI-2118-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016841 | PS5-71-BI-2118-CC01 | C | I | No Outdoor Metal Cable Tag | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016844 | PS5-71-BI-2119-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016846 | PS5-71-BI-2119-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016848 | PS5-71-BI-2120-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016849 | PS5-71-BI-2120-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016850 | PS5-71-BI-2120-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016852 | PS5-71-BI-2120-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016853 | PS5-71-BI-2120-CC01 | C | I | No Outdoor Metal Cable Tag | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016855 | PS5-71-BI-2121-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016856 | PS5-71-BI-2121-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016857 | PS5-71-BI-2121-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016858 | PS5-71-BI-2121-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016859 | PS5-71-BI-2121-CC01 | C | I | No Outdoor Metal Cable Tag | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016861 | PS5-71-BI-2121-CC01 | B | I | No Proper Cable Dressing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016862 | PS5-71-BI-2122-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016864 | PS5-71-BI-2122-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016865 | PS5-71-BI-2122-CC01 | B | I | No proper Cable Dressing (Below Unistrut channel Missing) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016875 | PS5-60-23_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-23 - Instrument Air Distribution lines
PL-016876 | PS5-60-23_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-23 - Instrument Air Distribution lines
PL-016900 | PS5-60-58_SS_ALL_LINES | B | P | 16: VALVE,FLANGE TO BE DONE | Originated |  | PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B
PL-016901 |  | B | P | 18:TZ-MID-68-WPR2-207154 - F15 Flange management to be done after Vendor installing PG | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-016906 |  | C | P | 18:TZ-MID-68-WPR2-206319 - ITEM 14, Bolt projection threads are at the same level | Originated |  | PS5-01-03 - Fire Water Pump B
PL-016925 |  | B | P | 18:TZ-MID-68-WPR2-207153 - F15 Flange management to be done after PG installed by vendor | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-016936 |  | C | P | 18:TZ-MID-68-WPR2-206318 - Item 14, Bolt projection threads are at the same level | Originated |  | PS5-01-02 - Fire Water Pump A
PL-016946 | PS5-71-BI-2123-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016948 | PS5-71-BI-2123-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016954 | PS5-71-BI-2124-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016955 | PS5-71-BI-2124-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016956 | PS5-71-BI-2125-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016957 |  | B | P | 18:TZ-MID-68-WPR2-206265 - Item 14, LEVER/HANDWHEEL ORI= E, RLMU tobe done | Originated |  | PS5-01-04 - Fire Water Pump Mini Flow Recycle
PL-016959 | PS5-71-BI-2125-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016960 |  | B | P | 18.1:TZ-MID-68-WPR2-206288 - ITEM 14, LEVER/HANDWHEEL ORI= E, RLMU tobe done | Originated |  | PS5-01-04 - Fire Water Pump Mini Flow Recycle
PL-016961 | PS5-71-BI-2125-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-016984 |  | B | P | 18: TZ-MID-68-WPR2-206288 - Item 14, LEVER/HANDWHEEL ORI= E, RLMU tobe done | Originated |  | PS5-01-03 - Fire Water Pump B
PL-016985 | PS5-01-TR-4100A | C | M | 23:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-01-02 - Fire Water Pump A
PL-016987 | PS5-01-TR-4100A | B | E | 23.1:EARTHING TO BE DONE | Originated |  | PS5-01-02 - Fire Water Pump A
PL-016990 |  | B | P | 18:TZ-MID-68-WPR2-207026 & TZ-MID-68-WPR2-207027 - F15 Flange Management to be done(PG in vender Scope) | Originated |  | PS5-01-01 - Fire Water Jockey Pump A/B
PL-016992 | PS5-01-TR-4100B | C | M | 23:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-01-03 - Fire Water Pump B
PL-016993 | PS5-01-TR-4100B | B | E | 23.1:EARTHING TO BE DONE | Originated |  | PS5-01-03 - Fire Water Pump B
PL-017017 |  | B | P | 18:TZ-MID-68-WPR2-206382 & TZ-MID-68-WPR2-206382 - Item 14, LEVER/HANDWHEEL ORI= N, RLMU tobe done | Originated |  | PS5-01-07 - Fire Water Ring Main & Distribution
PL-017018 | PS5-03-BI-2503-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017019 | PS5-03-BI-2503-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017020 | PS5-03-BI-2503-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017025 | PS5-28-VDC-1400 | C | M | 18:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-017026 | PS5-28-VDC-1400 | B | E | 18.1:EARTHING TO BE DONE | Originated |  | PS5-28-04 - Closed Drain Drum and Pump 02
PL-017044 | PS5-03-BI-2509-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017045 | PS5-03-BI-2509-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017046 | PS5-03-BI-2509-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017047 | PS5-03-BI-2509-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017048 | PS5-25-BI-1101-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017049 | PS5-25-BI-1101-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017050 | PS5-25-BI-1101-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017051 | PS5-25-BI-1102-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017052 | PS5-25-BI-1102-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017053 | PS5-25-BI-1102-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017054 | PS5-25-BI-1103-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017055 | PS5-25-BI-1103-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017056 | PS5-25-BI-1103-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017057 | PS5-25-BI-1104-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017058 | PS5-25-BI-1104-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017059 | PS5-25-BI-1104-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017060 | PS5-25-BI-1201-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017061 | PS5-25-BI-1201-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017062 | PS5-25-BI-1201-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017063 | PS5-25-BI-1201-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017066 | PS5-01-IE-0009A-CL01 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-01-02 - Fire Water Pump A
PL-017067 | PS5-01-IE-0009A-CL01 | B | E | No Proper Earth | Originated |  | PS5-01-02 - Fire Water Pump A
PL-017068 | PS5-01-IE-0009A-CL01 | B | E | No Cable’s Core Marker | Originated |  | PS5-01-02 - Fire Water Pump A
PL-017071 | PS5-60-TX-41500A | C | M | 23:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-017072 | PS5-60-TX-41500A | B | E | 23.1:EARTHING TO BE DONE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-017110 | PS5-60-TX-41500B | B | E | 23:EARTHING TO BE DONE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-017111 | PS5-60-TX-41500B | C | M | 23.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-74 - Engine E Cooling system
PL-017115 | PS5-60-TX-41600A | C | M | 23:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-017116 | PS5-60-TX-41600A | B | E | 23.1:EARTHING TO BE DONE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-017117 | PS5-60-TX-41600B | B | E | 23:EARTHING TO BE DONE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-017118 | PS5-60-TX-41600B | C | P | 23.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-75 - Engine F Cooling system
PL-017122 | PS5-60-TX-41700A | C | M | 23TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-017124 | PS5-60-TX-41700A | B | E | 23.1: EARTHING TO BE DONE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-017126 | PS5-60-TX-41700B | B | E | 23: EARTHING TO BE DONE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-017127 | PS5-60-TX-41700B | C | M | 23.1:TOUCH UP PAINTING TO BE DONE | Originated |  | PS5-60-76 - Engine G Cooling system
PL-017161 | PS5-28-VDC-1100 | B | M | 18:TOUCH UP PAINTING & INSULATION TO BE DONE | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-017162 | PS5-28-VDC-1100 | B | E | 18.1:EARTHING TO BE DONE | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-017164 | PS5-01-BI-1118-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017165 | PS5-01-BI-1118-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017166 | PS5-01-BI-1118-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017172 | PS5-25-BI-2103-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017173 | PS5-25-BI-2103-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017174 | PS5-25-BI-2103-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017175 | PS5-28-BI-1303-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017177 | PS5-28-BI-1303-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017178 | PS5-28-BI-1303-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017182 | PS5-50-BI-1107-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017184 | PS5-50-BI-1107-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017186 | PS5-50-BI-1107-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017256 | PS5-53-BI-1108-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017257 | PS5-53-BI-1108-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017258 | PS5-53-BI-1108-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017259 | PS5-53-BI-1108-CC01 | B | I | No Proper Cable Dressing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017260 | PS5-71-BI-1111-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017261 | PS5-71-BI-1111-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017262 | PS5-71-BI-1111-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017263 | PS5-71-BI-2116-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017265 | PS5-71-BI-2116-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017266 | PS5-71-BI-2116-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017268 | PS5-71-BI-2310-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017269 | PS5-71-BI-2310-CC01 | C | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017270 | PS5-71-BI-2310-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017271 | PS5-71-BI-2310-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017276 | PS5-60-30_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-017277 | PS5-60-30_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-30 - Air Receiver C & Air Regulator C
PL-017278 | PS5-60-31_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-017279 | PS5-60-31_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-31 - Air Receiver D & Air Regulator D
PL-017280 | PS5-60-IE-0004-CC08 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017281 | PS5-60-IE-0004-CC08 | B | I | No Proper Screen Earth | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017282 | PS5-60-IE-0004-CC08 | B | I | No Proper MCT Packing | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017354 | PS5-71-08_SS_ALL_LINES | B | P | 6:TP-309 -Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-017355 | PS5-71-08_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-71-08 - CFO Pre-Pressure Modules
PL-017358 | PS5-60-07_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-07 - Power Generation Package C
PL-017360 | PS5-60-07_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-07 - Power Generation Package C
PL-017366 | PS5-60-73_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-73 - Engine D Cooling system
PL-017367 | PS5-60-73_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-73 - Engine D Cooling system
PL-017369 | PS5-60-72_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-72 - Engine C Cooling system
PL-017370 | PS5-60-72_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-72 - Engine C Cooling system
PL-017371 | PS5-60-10_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-10 - Power Generation Package D
PL-017372 | PS5-60-10_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-10 - Power Generation Package D
PL-017373 | PS5-60-IE-0004-CC11 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017374 | PS5-60-IE-0004-CC11 | B | I | No Proper Screen Earth | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017375 | PS5-60-IE-0004-CC11 | B | I | No Proper MCT Packing | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017376 | PS5-60-IE-0004-CC11 | B | I | Wrong Cable’s Core Marker | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017377 | PS5-60-IE-0004-CC12 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017378 | PS5-60-IE-0004-CC12 | B | I | No Proper Screen Earth | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017379 | PS5-60-IE-0004-CC12 | B | I | No Proper MCT Packing | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017380 | PS5-60-IE-0004-CC12 | B | I | No Cable’s Core Marker | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017381 | PS5-60-TX-41500A | B | M | 23.2:Blind flange to be installed downstream of the drain valve Engineering / Vendor | Originated |  | PS5-60-74 - Engine E Cooling system
PL-017403 | PS5-60-TX-41500B | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | Originated |  | PS5-60-74 - Engine E Cooling system
PL-017404 | PS5-60-TX-41600A | B | P | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | Originated |  | PS5-60-75 - Engine F Cooling system
PL-017405 | PS5-60-TX-41600B | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | Originated |  | PS5-60-75 - Engine F Cooling system
PL-017406 | PS5-60-TX-41700A | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | Originated |  | PS5-60-76 - Engine G Cooling system
PL-017407 | PS5-60-TX-41700B | B | M | 23.2:Blind flange to be installed downstream of the drain valve . (Engineering / Vendor) | Originated |  | PS5-60-76 - Engine G Cooling system
PL-017472 |  | B | P | 18:TZ-MID-68-WPR2-206380 - Item 07 & 08, WN FLG & Gasket, CL300 RLMU to be done | Originated |  | PS5-28-05 - HP Relief Header
PL-017473 |  | B | P | 18.1:TZ-MID-68-WPR2-206380 - F4 & F5 Flange Management to be done | Originated |  | PS5-28-05 - HP Relief Header
PL-017480 | PS5-28-VK-1200 | B | E | 18: Electrical heating cable to be installed | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-017481 | PS5-28-VK-1200 | B | P | 18.1:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-017483 | PS5-28-VK-1200 | C | M | 18.2: Hot insulation to be done by Insulation team | Originated |  | PS5-28-06 - Relief Drum and Pump
PL-017485 | PS5-74-VA-1100 | C | M | 18:TOUCH UP PAINTING TO BE COMPLETED WHEREVER REQUIRED ON THE EQUIPMENT | Originated |  | PS5-74-03 - Nitrogen Receiver
PL-017486 | PS5-74-VA-1100 | B | E | 18.1: EARTHING TO BE DONE | Originated |  | PS5-74-03 - Nitrogen Receiver
PL-017487 | PS5-53-TR-4100 | B | P | 23:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-53-01 - Utility Water / Storage Tank
PL-017488 |  | B | P | 18: UB02 Clamp support to be install 1 nos | Originated |  | PS5-01-10 - Water Mist Package
PL-017528 | PS5-25-BI-2302-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017529 | PS5-25-BI-2302-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017530 | PS5-25-BI-2302-CC01 | B | I | No Cable’s Core Marker | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017531 | PS5-25-BI-2302-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017532 | PS5-28-BI-1105-CC01 | C | I | No indoor cable tag (Yellow Black) | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017533 | PS5-28-BI-1105-CC01 | B | I | No Proper Screen Earth | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017534 | PS5-28-BI-1105-CC01 | B | I | No Proper MCT Packing | Originated |  | PS5-91-01 - Multicore cables & JB
PL-017554 | PS5-60-IE-0003B-CD06 | C | E | No Indoor Cable Tag (Yellow Black) | Originated |  | PS5-60-04 - Power Generation Package B
PL-017557 | PS5-60-IE-0003B-CD08 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-04 - Power Generation Package B
PL-017558 | PS5-60-IE-0003B-CD08 | B | E | No Cable’s Core Marker for Blue Core | Originated |  | PS5-60-04 - Power Generation Package B
PL-017560 | PS5-60-IE-0003B-CD12 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-04 - Power Generation Package B
PL-017561 | PS5-60-IE-0003B-CD12 | B | E | Earh core not connected | Originated |  | PS5-60-04 - Power Generation Package B
PL-017563 | PS5-60-IE-0003C-CD08 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-07 - Power Generation Package C
PL-017574 | PS5-60-IE-0004-CD01 | B | E | Earth core not connected | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017578 | PS5-60-IE-0004-CD01 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017582 | PS5-60-IE-0004-CD02 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017583 | PS5-60-IE-0004-CD02 | B | E | Earth Core is not Connected | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017587 | PS5-60-IE-0004-CD14 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017588 | PS5-60-IE-0004-CD14 | B | E | No Cable’s Core Marker | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017591 | PS5-78-JC-9100D | B | E | 17:PUNCH LIST ID PL-001470,PL-001475,PL-004419,PL-004420,PL-004426 TO BE CLOSED | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-017592 | PS5-78-JC-9100D | C | M | 17.1: PUNCH LIST ID PL-001469,PL-004343 TO BE CLOSED | Originated |  | PS5-78-01 - Lifting and handling equipment
PL-017600 | PS5-28-VDC-1100 | B | P | 18.2:Thermowells (Nozzle K1, K2) to be installed after GALT test | Originated |  | PS5-28-03 - Closed Drain Drum and Pump 01
PL-017603 | PS5-25-SPZS-0002A | C | M | 16:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-25-02 - Crude Oil Export Pump A
PL-017605 | PS5-25-SPZS-0002B | C | M | 16:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-25-03 - Crude Oil Export Pump B
PL-017606 | PS5-25-SPZS-0002C | C | M | 16:Touch up / painting to be completed wherever required on the equipment | Originated |  | PS5-25-04 - Crude Oil Export Pump C
PL-017630 | PS5-60-37_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-017636 | PS5-60-37_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-37 - Injector Tip Cooling Module C
PL-017642 | PS5-60-38_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-017644 | PS5-60-38_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-38 - Injector Tip Cooling Module D
PL-017652 | PS5-60-52_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-017655 | PS5-60-52_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D
PL-017664 | PS5-60-62_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-017665 | PS5-60-62_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D
PL-017668 | PS5-60-60_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-017669 | PS5-60-60_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C
PL-017680 | PS5-60-IE-0004-CD15 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017682 | PS5-60-IE-0004-CD15 | B | E | No Cable’s Core Marker | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017684 | PS5-60-IE-0004-CD15 | B | E | Unused cores not properly protected (Including screen & Earth) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017685 | PS5-60-BE-0021A-CL01 | B | E | TERMINTION NOT COMPLET Chimney Aviation Lights JB PS5-60-BE-0021A | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017686 | PS5-60-IE-0004-CD15 | B | E | No Earthing for Gland's Earth tag | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017688 | PS5-60-IE-0004-CD15 | C | E | No outdoor Cable Tag | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017689 | PS5-60-BE-0021B-CL01 | B | E | TERMINTION NOT COMPLET Chimney Aviation Lights JB PS5-60-BE-0021B | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017693 | PS5-60-IE-0004-CD16 | C | E | No indoor cable tag (Yellow Black) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017694 | PS5-60-IE-0004-CD16 | B | E | No Cable’s Core Marker | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017695 | PS5-60-IE-0004-CD16 | B | E | No Earthing for Gland's Earth tag | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017696 | PS5-60-IE-0004-CD16 | B | E | Unused cores not properly protected (Including screen & Earth) | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017697 | PS5-60-IE-0004-CD16 | C | E | No outdoor Metal cable tag | Originated |  | PS5-60-22 - Power Gen Master UCP
PL-017698 | PS5-60-BI-0001C-CC02 | B | I | TERMINTION NOT COMPLET 60-IE-0001C TB 24,31,15 | Originated |  | PS5-60-07 - Power Generation Package C
PL-017699 | PS5-60-BI-0010A-CC01 | B | I | TERMINAL BLOCK ISSUE / in complet DWG ISSUE | Originated |  | PS5-60-07 - Power Generation Package C
PL-017700 | PS5-09-QX-8451A | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-017701 | PS5-60-IE-0002C-CC01 | B | I | 60-IE-0002C SIDE LDP SIDE NOT TERMINTED | Originated |  | PS5-60-07 - Power Generation Package C
PL-017702 | PS5-09-QX-8451A | B | H | 16.1: HVAC ducting installation to be done | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-017703 | PS5-60-IE-0002C-CC02 | B | I | TERMINTION NOT COMPLET 60-IE-0002C TB 1,2,3 | Originated |  | PS5-60-07 - Power Generation Package C
PL-017705 | PS5-09-QX-8451A | B | E | 16.2:Earthing to be done | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-017706 | PS5-09-QX-8451B | B | P | 16:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-017707 | PS5-09-QX-8451B | B | H | 16.1:HVAC ducting installation to be done | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-017708 | PS5-60-IE-0003C-CC16 | B | I | TERMINATION WRONG DWG ISSUE | Originated |  | PS5-60-08 - Power Gen Package C (UCP)
PL-017709 | PS5-09-QX-8451B | B | E | 16.2: Earthing to be done | Originated |  | PS5-09-03 - HVAC for Generator Building
PL-017710 | PS5-61-BI-0003-CC01 | B | I | TERMINATION WRONG DWG ISSUE | Originated |  | PS5-60-07 - Power Generation Package C
PL-017711 | PS5-71-IN-0001-CC06 | B | I | PS5 -60-IE-0004 TBX1501-5,6 Termination DWG ISSUE | Originated |  | PS5-71-19 - Diesel Separator Module (UCP)
PL-017714 |  | B | P | 18:Manhole cover to be installed and properly closed. | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-017719 |  | B | P | 18:Manhole cover to be installed and properly closed. | Originated |  | PS5-28-07 - Open Drains (OD2)
PL-017775 | PS5-60-44_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-017776 | PS5-60-44_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C
PL-017779 | PS5-60-45_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-017780 | PS5-60-45_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D
PL-017781 | PS5-60-51_SS_ALL_LINES | B | P | 6:Final coating shall be defect free. (Repair damage/scratches and maintain uniform appearance) | Originated |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-017782 | PS5-60-51_SS_ALL_LINES | C | P | 6.1:Stenciling to be done | Originated |  | PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C
PL-017863 | PS5-50-SPZQ-0027 | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-50-03 - Water Pre-Treatment Package
PL-017864 | PS5-71-SPZQ-0026 | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-71-16 - Diesel Fuel Supply Pump A/B
PL-017865 | PS5-28-UO-8200 | B | P | 8:FINAL PIPING CONNECTION AND REINSTATEMENT TO BE COMPLETED AFTER HT(descipiline-piping) | Originated |  | PS5-28-11 - Open Drain Interceptor

## SIDMAP (hidden)
PS5-01-01 - Fire Water Jockey Pump A/B | PS5-01-01
PS5-01-02 - Fire Water Pump A | PS5-01-02
PS5-01-03 - Fire Water Pump B | PS5-01-03
PS5-01-04 - Fire Water Pump Mini Flow Recycle | PS5-01-04
PS5-01-05 - Foam Skid | PS5-01-05
PS5-01-06 - Foam Concentrate Distribution | PS5-01-06
PS5-01-07 - Fire Water Ring Main & Distribution | PS5-01-07
PS5-01-08 - PS5 Deluge Valve Skid (PS5-01-UK-6100) | PS5-01-08
PS5-01-09 - Inergen for EITS Building | PS5-01-09
PS5-01-10 - Water Mist Package | PS5-01-10
PS5-01-11 - Inergen for Power Gen Building | PS5-01-11
PS5-02-01 - Miscellaneous Safety equipment | PS5-02-01
PS5-02-02 - Portable Fire Fighting Equipments | PS5-02-02
PS5-03-01 - FZ-01 - Process Area | PS5-03-01
PS5-03-03 - FZ-03 - Buildings Area | PS5-03-03
PS5-03-04 - FZ-04 - Utilities - Diesel and Firewater Pumps Areas | PS5-03-04
PS5-03-06 - FZ-06 - Transformer Area | PS5-03-06
PS5-03-07 - FZ-07 - Pretreatment Area | PS5-03-07
PS5-03-08 - FZ-08 - Utilities - Power Generation Area - External | PS5-03-08
PS5-03-09 - FZ-09 - Power Generation Building - Engine Bay 1 | PS5-03-09
PS5-03-10 - FZ-10 - Power Generation Building - Engine Bay 2 | PS5-03-10
PS5-03-11 - FZ-11 - Power Generation Building - Engine Bay 3 | PS5-03-11
PS5-03-12 - FZ-12 - Power Generation Building - Engine Bay 4 | PS5-03-12
PS5-03-13 - FZ-13 - Power Generation Building - Instrument Air Room | PS5-03-13
PS5-03-14 - FZ-14 - Power Generation Building - Switchgear Room | PS5-03-14
PS5-03-15 - FZ-15 - Power Generation Building - Generator Room 1 | PS5-03-15
PS5-03-16 - FZ-16 - Power Generation Building - Generator Room 2 | PS5-03-16
PS5-03-17 - FZ-17 - Power Generation Building - Generator Room 3 | PS5-03-17
PS5-03-18 - FZ-18 - Power Generation Building - Generator Room 4 | PS5-03-18
PS5-03-19 - FZ-19 - Power Generation Building - Battery Room | PS5-03-19
PS5-03-20 - FZ-20 - Emergency Diesel Generator Enclosure | PS5-03-20
PS5-03-21 - FZ-21 - Power Generation Building - Air Handling Unit | PS5-03-21
PS5-03-22 - FZ-G1 - Guard House | PS5-03-22
PS5-03-23 - FZ-E1 to E3 - EITS Building | PS5-03-23
PS5-03-24 - FZ - Office and Facilities Building | PS5-03-24
PS5-03-25 - FZ - Workshop & Warehouse | PS5-03-25
PS5-04-01 - Office Building PCS System | PS5-04-01
PS5-04-02 - Office Building SIS/FGS System | PS5-04-02
PS5-04-03 - 33kV ICSS System | PS5-04-03
PS5-04-04 - 33kV PCS System | PS5-04-04
PS5-04-05 - 33kV SIS/FGS System | PS5-04-05
PS5-05-01 - Emergency Diesel Generator Package | PS5-05-01
PS5-05-02 - Emergency Diesel Generator Package (UCP) | PS5-05-02
PS5-06-01 - AC UPS - EITS Building | PS5-06-01
PS5-06-02 - AC UPS - Power Generator Building | PS5-06-02
PS5-06-03 - AC UPS - Office & Facilities Building | PS5-06-03
PS5-06-04 - AC UPS - Guard House | PS5-06-04
PS5-06-05 - AC UPS - Workshop & Warehouse | PS5-06-05
PS5-08-01 | PS5-08-01
PS5-08-01a - PAGA (Required for SU) | PS5-08-01a
PS5-08-01b - PAGA (Not required for SU) | PS5-08-01b
PS5-08-03 - Telephone | PS5-08-03
PS5-08-04 - Hotline | PS5-08-04
PS5-08-07 - Multi-Channel Voice Recorder | PS5-08-07
PS5-08-11 - Corporate LAN (SIE) | PS5-08-11
PS5-08-12 - Corporate Wireless LAN (SIE) | PS5-08-12
PS5-08-13 - Safety Data Network (SII SP3 SAF) | PS5-08-13
PS5-08-14 - Industrial Data Network (SII SP1) | PS5-08-14
PS5-08-15 - Security Data Network (SII SP3 SEC) | PS5-08-15
PS5-08-23 - VHF Trunk Radio System | PS5-08-23
PS5-08-34 - Satphone | PS5-08-34
PS5-08-35 - Optical Transport Network | PS5-08-35
PS5-08-36 - Pipeline FO Cable & EPRS | PS5-08-36
PS5-08-51 - Entertainment | PS5-08-51
PS5-08-52a - Process & Security CCTV (Required for SU) | PS5-08-52a
PS5-08-52b - Process & Security CCTV (Not required for SU) | PS5-08-52b
PS5-08-55 - Videoconference | PS5-08-55
PS5-08-61 - Meteocean | PS5-08-61
PS5-08-71 - Structured Cabling (CAT6) | PS5-08-71
PS5-08-72 - Structured Cabling (FO) | PS5-08-72
PS5-08-81 - Guard tour | PS5-08-81
PS5-08-82 - Key Management | PS5-08-82
PS5-08-83 - Perimeter & Pipeline intrusion detection system | PS5-08-83
PS5-08-85 | PS5-08-85
PS5-08-85a - Access Control, POB & e-Mustering (Required for SU) | PS5-08-85a
PS5-08-85b - Access Control, POB & e-Mustering (Not required for SU) | PS5-08-85b
PS5-08-86 - Integrated Security Management System | PS5-08-86
PS5-08-92 - Telecom Mast | PS5-08-92
PS5-08-93 - Telecom Monitoring System | PS5-08-93
PS5-09-01 - HVAC for Office and Facilities building | PS5-09-01
PS5-09-02 - HVAC for Guard House | PS5-09-02
PS5-09-03 - HVAC for Generator Building | PS5-09-03
PS5-09-04 - HVAC for Workshop & Warehouse | PS5-09-04
PS5-09-05 - HVAC for EITS Building | PS5-09-05
PS5-0H-01 - HIPPS | PS5-0H-01
PS5-25-01 - Export Pipeline Pig Receiver | PS5-25-01
PS5-25-02 - Crude Oil Export Pump A | PS5-25-02
PS5-25-03 - Crude Oil Export Pump B | PS5-25-03
PS5-25-04 - Crude Oil Export Pump C | PS5-25-04
PS5-25-05 - Crude Oil Export Pumps Bypass | PS5-25-05
PS5-25-06 - Crude Oil Export Pumps Discharge | PS5-25-06
PS5-25-07 - Export Pipeline Pig Launcher | PS5-25-07
PS5-28-01 - Closed Drain Header 1 | PS5-28-01
PS5-28-02 - Closed Drain Header 2 | PS5-28-02
PS5-28-03 - Closed Drain Drum and Pump 01 | PS5-28-03
PS5-28-04 - Closed Drain Drum and Pump 02 | PS5-28-04
PS5-28-05 - HP Relief Header | PS5-28-05
PS5-28-06 - Relief Drum and Pump | PS5-28-06
PS5-28-07 - Open Drains (OD2) | PS5-28-07
PS5-28-08 - Open Drain Sump and Pumps | PS5-28-08
PS5-28-09 - Observation Basin | PS5-28-09
PS5-28-10 - Oil Skimmer Package | PS5-28-10
PS5-28-11 - Open Drain Interceptor | PS5-28-11
PS5-28-12 - Open Drains (OD3) | PS5-28-12
PS5-28-13 - Seal Oil Drain Drum & Pump A | PS5-28-13
PS5-28-14 - Seal Oil Drain Drum & Pump B | PS5-28-14
PS5-28-15 - Seal Oil Drain Drum & Pump C | PS5-28-15
PS5-28-16 - LP Relief Header | PS5-28-16
PS5-28-17 - Reinjection Pump | PS5-28-17
PS5-50-01 - Water Well Submersible Pumps (3100) | PS5-50-01
PS5-50-02 - Water Well Submersible Pumps (3200) | PS5-50-02
PS5-50-03 - Water Pre-Treatment Package | PS5-50-03
PS5-53-01 - Utility Water / Storage Tank | PS5-53-01
PS5-53-02 - Water Distribution Pump A/B | PS5-53-02
PS5-53-03 - Water Softener Package | PS5-53-03
PS5-53-04 - Water Treatment Purification Package | PS5-53-04
PS5-53-05 - Water Distribution Header | PS5-53-05
PS5-53-06 - Water Distribution Consumers | PS5-53-06
PS5-60-01 - Power Generation Package A | PS5-60-01
PS5-60-02 - Power Gen Package A (UCP) | PS5-60-02
PS5-60-03 - Power Gen Package A Generator Auxiliary MCCs & DBs | PS5-60-03
PS5-60-04 - Power Generation Package B | PS5-60-04
PS5-60-05 - Power Gen Package B (UCP) | PS5-60-05
PS5-60-06 - Power Gen Package B Generator Auxiliary MCCs & DBs | PS5-60-06
PS5-60-07 - Power Generation Package C | PS5-60-07
PS5-60-08 - Power Gen Package C (UCP) | PS5-60-08
PS5-60-09 - Power Gen Package C Generator Auxiliary MCCs & DBs | PS5-60-09
PS5-60-10 - Power Generation Package D | PS5-60-10
PS5-60-11 - Power Gen Package D (UCP) | PS5-60-11
PS5-60-12 - Power Gen Package D Generator Auxiliary MCCs & DBs | PS5-60-12
PS5-60-13 - Power Generation Package E | PS5-60-13
PS5-60-14 - Power Gen Package E (UCP) | PS5-60-14
PS5-60-15 - Power Gen Package E Generator Auxiliary MCCs & DBs | PS5-60-15
PS5-60-16 - Power Generation Package F | PS5-60-16
PS5-60-17 - Power Gen Package F (UCP) | PS5-60-17
PS5-60-18 - Power Gen Package F Generator Auxiliary MCCs & DBs | PS5-60-18
PS5-60-19 - Power Generation Package G | PS5-60-19
PS5-60-20 - Power Gen Package G (UCP) | PS5-60-20
PS5-60-21 - Power Gen Package G Generator Auxiliary MCCs & DBs | PS5-60-21
PS5-60-22 - Power Gen Master UCP | PS5-60-22
PS5-60-23 - Instrument Air Distribution lines | PS5-60-23
PS5-60-24 - Cooling Water Tank & Pump | PS5-60-24
PS5-60-25 - Cooling Water Maintenance Tank & Return Pump | PS5-60-25
PS5-60-26 - Instrument Air Compressor Skid | PS5-60-26
PS5-60-27 - Compressed Air Starting Skid | PS5-60-27
PS5-60-28 - Air Receiver A & Air Regulator A | PS5-60-28
PS5-60-29 - Air Receiver B & Air Regulator B | PS5-60-29
PS5-60-30 - Air Receiver C & Air Regulator C | PS5-60-30
PS5-60-31 - Air Receiver D & Air Regulator D | PS5-60-31
PS5-60-32 - Air Receiver E & Air Regulator E | PS5-60-32
PS5-60-33 - Air Receiver F & Air Regulator F | PS5-60-33
PS5-60-34 - Air Receiver G & Air Regulator G | PS5-60-34
PS5-60-35 - Injector Tip Cooling Module A | PS5-60-35
PS5-60-36 - Injector Tip Cooling Module B | PS5-60-36
PS5-60-37 - Injector Tip Cooling Module C | PS5-60-37
PS5-60-38 - Injector Tip Cooling Module D | PS5-60-38
PS5-60-39 - Injector Tip Cooling Module E | PS5-60-39
PS5-60-40 - Injector Tip Cooling Module F | PS5-60-40
PS5-60-41 - Injector Tip Cooling Module G | PS5-60-41
PS5-60-42 - Oil Mist Separator Skid PS5-60-VS-9100A | PS5-60-42
PS5-60-43 - Oil Mist Separator Skid PS5-60-VS-9100B | PS5-60-43
PS5-60-44 - Oil Mist Separator Skid PS5-60-VS-9100C | PS5-60-44
PS5-60-45 - Oil Mist Separator Skid PS5-60-VS-9100D | PS5-60-45
PS5-60-46 - Oil Mist Separator Skid PS5-60-VS-9100E | PS5-60-46
PS5-60-47 - Oil Mist Separator Skid PS5-60-VS-9100F | PS5-60-47
PS5-60-48 - Oil Mist Separator Skid PS5-60-VS-9100G | PS5-60-48
PS5-60-49 - Lube Oil Separator Module PS5-60-UO-81100A | PS5-60-49
PS5-60-50 - Lube Oil Separator Module PS5-60-UO-81100B | PS5-60-50
PS5-60-51 - Lube Oil Separator Module PS5-60-UO-81100C | PS5-60-51
PS5-60-52 - Lube Oil Separator Module PS5-60-UO-81100D | PS5-60-52
PS5-60-53 - Lube Oil Separator Module PS5-60-UO-81100E | PS5-60-53
PS5-60-54 - Lube Oil Separator Module PS5-60-UO-81100F | PS5-60-54
PS5-60-55 - Lube Oil Separator Module PS5-60-UO-81100G | PS5-60-55
PS5-60-56 - Fuel Conditioning Module PS5-60-UZ-8900A | PS5-60-56
PS5-60-57 - Fuel Conditioning Module PS5-60-UZ-8900A (UCP) | PS5-60-57
PS5-60-58 - Fuel Conditioning Module PS5-60-UZ-8900B | PS5-60-58
PS5-60-59 - Fuel Conditioning Module PS5-60-UZ-8900B (UCP) | PS5-60-59
PS5-60-60 - Fuel Conditioning Module PS5-60-UZ-8900C | PS5-60-60
PS5-60-61 - Fuel Conditioning Module PS5-60-UZ-8900C (UCP) | PS5-60-61
PS5-60-62 - Fuel Conditioning Module PS5-60-UZ-8900D | PS5-60-62
PS5-60-63 - Fuel Conditioning Module PS5-60-UZ-8900D (UCP) | PS5-60-63
PS5-60-64 - Fuel Conditioning Module PS5-60-UZ-8900E | PS5-60-64
PS5-60-65 - Fuel Conditioning Module PS5-60-UZ-8900E (UCP) | PS5-60-65
PS5-60-66 - Fuel Conditioning Module PS5-60-UZ-8900F | PS5-60-66
PS5-60-67 - Fuel Conditioning Module PS5-60-UZ-8900F (UCP) | PS5-60-67
PS5-60-68 - Fuel Conditioning Module PS5-60-UZ-8900G | PS5-60-68
PS5-60-69 - Fuel Conditioning Module PS5-60-UZ-8900G (UCP) | PS5-60-69
PS5-60-70 - Engine A Cooling system | PS5-60-70
PS5-60-71 - Engine B Cooling system | PS5-60-71
PS5-60-72 - Engine C Cooling system | PS5-60-72
PS5-60-73 - Engine D Cooling system | PS5-60-73
PS5-60-74 - Engine E Cooling system | PS5-60-74
PS5-60-75 - Engine F Cooling system | PS5-60-75
PS5-60-76 - Engine G Cooling system | PS5-60-76
PS5-61-01 - 33kV Switchboard EITS Building (PS5-61-IJ-0001) | PS5-61-01
PS5-61-02 - 6.6kV Switchboard and Transformer LLHT North - EITS Building (PS5-61-IJ-0010) | PS5-61-02
PS5-61-03 - 6.6kV Switchboard and Transformer LLHT South - EITS Building (PS5-61-IJ-0011) | PS5-61-03
PS5-61-04 - 0.4kV Switchboard Office & Facilities Building (PS5-61-IK-0005) | PS5-61-04
PS5-61-05 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0003) | PS5-61-05
PS5-61-06 - 0.4kV Switchboard Power Generator Building (PS5-61-IK-0006) | PS5-61-06
PS5-61-07 - 0.4kV Switchboard EITS Building (PS5-61-IK-0001) | PS5-61-07
PS5-61-08 - Electrical Control System | PS5-61-08
PS5-61-09 - Outdoor Power Distribution Board - PS5-61-IG-0014 | PS5-61-09
PS5-61-10 - Outdoor Valves Distribution Board - PS5-61-IG-0042 | PS5-61-10
PS5-61-11 - Outdoor Valves Distribution Board - PS5-61-IG-0043 | PS5-61-11
PS5-61-12 - EITS 33kV Bld. Normal Auxiliary DP - PS5-61-IG-0008 | PS5-61-12
PS5-61-13 - Power Distribution Board Office Building - PS5-61-IG-0020 | PS5-61-13
PS5-61-14 - Power Distribution Board Workshop & Warehouse - PS5-61-IG-0009 | PS5-61-14
PS5-62-01 - Lighting Control Panel - PS5-62-IE-0001 | PS5-62-01
PS5-62-02 - Lighting Control Panel - PS5-62-IE-0002 | PS5-62-02
PS5-62-03 - Outdoor Emergency Lighting DB - PS5-05-IG-0004 | PS5-62-03
PS5-62-04 - Outdoor Emergency Lighting DB - PS5-05-IG-0006 | PS5-62-04
PS5-62-05 - Guard House Emergency L&SP DB - PS5-05-IG-0007 | PS5-62-05
PS5-62-06 - CRO Generator Building Emergency Lighting DB - PS5-05-IG-0025 | PS5-62-06
PS5-62-07 - CRO Generator Electrical Building Emergency Lighting DB - PS5-05-IG-0026 | PS5-62-07
PS5-62-08 - Outdoor Normal Lighting DB - PS5-61-IG-0006 | PS5-62-08
PS5-62-09 - Outdoor Normal Lighting DB - PS5-61-IG-0007 | PS5-62-09
PS5-62-10 - CRO Generator Building Normal L&SP DB - PS5-61-IG-0015 | PS5-62-10
PS5-62-11 - CRO Generator Electrical Building Normal L&SP DB - PS5-61-IG-0016 | PS5-62-11
PS5-62-12 - EITS 33kV Bld. Emergency L&SP DP - PS5-05-IG-0003 | PS5-62-12
PS5-62-13 - EITS 33kV Bld. Normal L&SP DP - PS5-61-IG-0003 | PS5-62-13
PS5-62-14 - Office Building Emergency L&SP DB - PS5-05-IG-0002 | PS5-62-14
PS5-62-15 - Office Building Normal L&SP DB - PS5-61-IG-0002 | PS5-62-15
PS5-62-16 - Guard Hut A Normal L&SP DB - PS5-61-IG-0111 | PS5-62-16
PS5-62-17 - Guard Hut B Normal L&SP DB - PS5-61-IG-0112 | PS5-62-17
PS5-62-18 - Workshop & Warehouse Normal L&SP DB - PS5-61-IG-0004 | PS5-62-18
PS5-62-19 - Workshop & Warehouse Emergency L&SP DB - PS5-05-IG-0101 | PS5-62-19
PS5-62-20 - Office Building Normal L&SP DB - PS5-61-IG-0010 | PS5-62-20
PS5-63-01 - Electrical Earthing | PS5-63-01
PS5-63-02 - Electrical Earthing - Office and Facilities building | PS5-63-02
PS5-63-03 - Electrical Earthing - Generator Building | PS5-63-03
PS5-63-04 - Electrical Earthing - EITS Building | PS5-63-04
PS5-63-05 - Electrical Earthing - Guard Hut A & B | PS5-63-05
PS5-63-06 - Electrical Earthing - Guard House | PS5-63-06
PS5-63-07 - Electrical Earthing - Workshop & Warehouse | PS5-63-07
PS5-71-01 - CFO Storage Tank Feed Heater | PS5-71-01
PS5-71-02 - CFO Allocation Metering Package | PS5-71-02
PS5-71-03 - CFO Allocation Metering Package (UCP) | PS5-71-03
PS5-71-04 - CFO Storage Tank | PS5-71-04
PS5-71-05 - CFO Transfer Pump A/B | PS5-71-05
PS5-71-06 - Crude Fuel Separation Module | PS5-71-06
PS5-71-07 - Crude Fuel Separation Module (UCP) | PS5-71-07
PS5-71-08 - CFO Pre-Pressure Modules | PS5-71-08
PS5-71-09 - CFO Pre-Pressure Modules (UCP) | PS5-71-09
PS5-71-12 - CFO Service Tank | PS5-71-12
PS5-71-13 - CFO Service Pump A/B | PS5-71-13
PS5-71-14 - Diesel Fuel Transfer and Dispensing Station | PS5-71-14
PS5-71-15 - Diesel Fuel Storage Tank | PS5-71-15
PS5-71-16 - Diesel Fuel Supply Pump A/B | PS5-71-16
PS5-71-17 - Diesel Fuel Distribution Header | PS5-71-17
PS5-71-18 - Diesel Separator Module | PS5-71-18
PS5-71-19 - Diesel Separator Module (UCP) | PS5-71-19
PS5-71-20 - Diesel Fuel Day Tank | PS5-71-20
PS5-71-21 - Diesel Transfer Pump A/B | PS5-71-21
PS5-71-22 - Diesel Fuel Pre Pressure Module | PS5-71-22
PS5-71-23 - Diesel Fuel Pre Pressure Module (UCP) | PS5-71-23
PS5-74-01 - N2 Generation Skid | PS5-74-01
PS5-74-02 - N2 Generation Skid (UCP) | PS5-74-02
PS5-74-03 - Nitrogen Receiver | PS5-74-03
PS5-74-04 - Nitrogen Distribution Header | PS5-74-04
PS5-75-01 - DRA Injection Package | PS5-75-01
PS5-75-02 - Biocide Injection Package | PS5-75-02
PS5-75-03 - Corrosion Inhibitor Injection Package | PS5-75-03
PS5-78-01 - Lifting and handling equipment | PS5-78-01
PS5-79-01 - Electrical Heat Tracing Transformer/Distribution Board 1 (PS5-79-IG-0001) | PS5-79-01
PS5-79-02 - Electrical Heat Tracing Transformer/Distribution Board 2 (PS5-79-IG-0002) | PS5-79-02
PS5-79-03 - Electrical Heat Tracing Transformer/Distribution Board 3 (PS5-79-IG-0003) | PS5-79-03
PS5-79-04 - Electrical Heat Tracing Transformer/Distribution Board 4 (PS5-79-IG-0004) | PS5-79-04
PS5-79-05 - Electrical Heat Tracing Transformer/Distribution Board 5 (PS5-79-IG-0005) | PS5-79-05
PS5-79-06 - Electrical Heat Tracing Transformer/Distribution Board 6 (PS5-79-IG-0006) | PS5-79-06
PS5-79-07 - Electrical Heat Tracing Transformer/Distribution Board 7 (PS5-79-IG-0007) | PS5-79-07
PS5-79-08 - Electrical Heat Tracing Transformer/Distribution Board 8 (PS5-79-IG-0008) | PS5-79-08
PS5-79-09 - Electrical Heat Tracing Transformer/Distribution Board 9 (PS5-79-IG-0009) | PS5-79-09
PS5-79-10 - Electrical Heat Tracing Transformer/Distribution Board 10 (PS5-79-IG-0010) | PS5-79-10
PS5-79-11 - Electrical Heat Tracing Transformer/Distribution Board 11 (PS5-79-IG-0011) | PS5-79-11
PS5-79-12 - Electrical Heat Tracing Transformer/Distribution Board 12 (PS5-79-IG-0012) | PS5-79-12
PS5-82-01 - Sanitary Sewage Collection | PS5-82-01
PS5-82-02 - Sewage Treatment Plant Package | PS5-82-02
PS5-82-03 - Sewage Treatment Plant Package (UCP) | PS5-82-03
PS5-82-04 - Sewage Treatment Plant Discharge Piping | PS5-82-04
PS5-82-05 - Office and Facilities building | PS5-82-05
PS5-82-06 - Guard House Building | PS5-82-06
PS5-82-07 - Guard Huts | PS5-82-07
PS5-83-01 - EITS Building | PS5-83-01
PS5-84-01 - Generator Building | PS5-84-01
PS5-84-02 - Workshop & Warehouse | PS5-84-02
PS5-84-03 - Shelters | PS5-84-03
PS5-86-01 - Shelters | PS5-86-01
PS5-91-01 - Multicore cables & JB | PS5-91-01
PS5-99-01 - Area Completion for Building area | PS5-99-01
PS5-99-02 - Area Completion for Utility area | PS5-99-02
PS5-99-03 - Area Completion for Power Distribution area | PS5-99-03
PS5-99-04 - Area Completion for Process area | PS5-99-04
PS5-99-05 - Area Completion for CFO area | PS5-99-05
PS5-99-06 - Area Completion for Power Generation area | PS5-99-06